## About
About — Plant water header — all cases (each case's solve and state: its Case block in this sheet) — SI base units
Section | Item | Value
Reading this file | Layout | Row 1 of each sheet is a caption and row 3 holds the headers (pandas: read_excel(..., sheet_name=None, header=2)).
Reading this file | Case and solve | Each row's case and solve: the Case, Solved at and Results columns.
Export | Title | OpenSolve Pipe results
Export | Project | Plant water header
Export | Project description | Export fixture: a tee, a PRV, a demand, a strainer and a cooler, with two scenarios.
Export | Exported at | 2026-10-25T14:32:05+02:00
Export | Contents | All cases
Export | Sheet: Flags | 0
Export | Sheet: Compare cases | 15
Export | Sheet: Nodes | 42
Export | Sheet: Links | 21
Export | Sheet: Pipes | 24
Export | Sheet: Fittings | 12
Export | Sheet: Valves | 3
Export | Sheet: Equipment | 6
Export | Sheet: Branches | 3
Export | Sheet: Branch ports | 9
Export | Sheet: Boundaries | 9
Export | Sheet: Boundary ports | 6
Export | Sheet: Assigned flows | 3
Export | Sheet: Scenario changes | 5
Export | Sheet: Methods | 403
Export | Units: elevations and lengths | m
Export | Units: diameters and roughness | m
Export | Units: heads, grade lines, losses and NPSH | m
Export | Units: gauge pressure | Pa(g)
Export | Units: absolute pressure | Pa(a)
Export | Units: pressure difference | Pa
Export | Units: flow | m³/s
Export | Units: velocity | m/s
Export | Units: temperature | K
Export | Units: density | kg/m³
Export | Units: dynamic viscosity | Pa·s
Export | Units: kinematic viscosity | m²/s
Export | Units: power | W
Export | Units: fractions (speed, efficiency, flow ÷ rated flow) | none (a pure number)
Export | Units: gauge and absolute | Pressures are gauge unless marked (a) or psia; differences carry no marker.
Export | Units: exceptions | The trace, the methods text, the server's flag messages and the JSON columns are in SI as the server reported them. The app's sentences (flag messages, the goal seek report) give speeds and efficiencies in % and powers in kW (hp with gpm). A Cv (US gpm of water at 1 psi) or Kv (m³/h of water at 1 bar) is as entered in every unit system.
Export | Units: fractions | Fractions (speed, efficiency) are 0–1 and carry no unit. Flow ÷ rated flow is a signed ratio with no unit: 1 at the rated flow, negative when the flow runs from outlet to inlet.
Export | Numbers | Full precision: each number is the value the calculation server returned, converted to these units, not rounded. The app shows 4 significant figures, and heads, elevations and lengths to at least 0.01 m (or its equivalent); it shows head differences below 1×10⁻⁷ m, valve and equipment pressure drops and equipment pressure losses below ρg·10⁻⁷ m and branch K below 1×10⁻⁴ as ≈ 0 (round-off). The file gives them as computed. Spreadsheets display and re-save at most 15 significant digits.
Export | Sign: link flow | + from → to
Export | Sign: valve flow | + inlet → outlet
Export | Sign: equipment flow | + inlet → outlet; flow ÷ rated flow, the pressure loss and the head loss are signed like it; the static pressure drop, inlet minus outlet, also holds the ports' elevation and velocity terms, so its sign need not follow the flow.
Export | Sign: pump flow | suction → discharge
Export | Sign: boundary outflow | + into the network
Export | Sign: assigned flow | + demand, − supply
Export | Sign: branch port flow | + into the branch
Export | Sign: losses | Losses are signed like the flow: negative where the flow runs to → from (outlet → inlet for valves); a branch path's loss is positive in the flow direction.
Export | Datum | Elevations and heads are measured from the project datum.
Not in this file | Trace | not in an All cases export: export one case to include it
Case: Base case | Status | Solved
Case: Base case | Values in this file | Yes
Case: Base case | Out of date | No
Case: Base case | Solved at | 2026-10-25T12:30:00Z
Case: Base case | Compute time [s] | 0.125
Case: Base case | Calculation methods version | 1.4.0
Case: Base case | Calculation methods changed | This project was last solved with calculation methods version 1.1.0. These results use version 1.4.0, so some values may differ from the ones it was shared with.
Case: Base case | Server library: CoolProp | 8.0.0
Case: Base case | Server library: fluids | 1.3.1
Case: Base case | Server library: numpy | 2.5.4
Case: Base case | Server library: opensolve-pipe | 0.1.0
Case: Base case | Server library: scipy | 1.18.1
Case: Base case | Converged | TRUE
Case: Base case | Inner iterations | 10
Case: Base case | Outer iterations | 2
Case: Base case | Largest continuity residual [m³/s] | 2.4807e-16
Case: Base case | Largest continuity residual at | E1:outlet
Case: Base case | Largest energy residual [m] | 1.3757e-12
Case: Base case | Largest energy residual at | L4
Case: Base case | Oscillating components | None
Case: Base case | Convergence message | converged: 10 Newton iterations in 2 outer iteration(s)
Case: Base case | Atmospheric pressure used [Pa(a)] | 99891.7297
Case: Base case | Site elevation [m] | 120
Case: Base case | Fluid | Water
Case: Base case | Fluid temperature [K] | 293.15
Case: Base case | Fluid concentration [mass fraction, 0–1]
Case: Base case | Fluid density [kg/m³] | 998.2072
Case: Base case | Fluid dynamic viscosity [Pa·s] | 0.0010016
Case: Base case | Fluid kinematic viscosity [m²/s] | 1.0034e-06
Case: Base case | Fluid vapor pressure [Pa(a)] | 2339.3182
Case: Base case | Source of the fluid's density | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Base case | Source of the fluid's dynamic viscosity | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
Case: Base case | Source of the fluid's vapor pressure | library: CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Base case | Lowest static pressure [Pa(g)] | 48945.3408
Case: Base case | Lowest static pressure at | Port 1 of Low tank_x0041_x0042_ (B)
Case: Base case | Highest velocity [m/s] | 2.6783
Case: Base case | Highest velocity in | Cooler (hot side) → -North main
Case: Base case | Project link | Link 1 below reproduces this case
Case: Cv valve (S1) | Status | Solved
Case: Cv valve (S1) | Values in this file | Yes
Case: Cv valve (S1) | Out of date | No
Case: Cv valve (S1) | Solved at | 2026-10-25T12:30:00Z
Case: Cv valve (S1) | Compute time [s] | 0.125
Case: Cv valve (S1) | Calculation methods version | 1.4.0
Case: Cv valve (S1) | Calculation methods changed | This project was last solved with calculation methods version 1.1.0. These results use version 1.4.0, so some values may differ from the ones it was shared with.
Case: Cv valve (S1) | Server library: CoolProp | 8.0.0
Case: Cv valve (S1) | Server library: fluids | 1.3.1
Case: Cv valve (S1) | Server library: numpy | 2.5.4
Case: Cv valve (S1) | Server library: opensolve-pipe | 0.1.0
Case: Cv valve (S1) | Server library: scipy | 1.18.1
Case: Cv valve (S1) | Converged | TRUE
Case: Cv valve (S1) | Inner iterations | 10
Case: Cv valve (S1) | Outer iterations | 2
Case: Cv valve (S1) | Largest continuity residual [m³/s] | 7.9624e-16
Case: Cv valve (S1) | Largest continuity residual at | E1:outlet
Case: Cv valve (S1) | Largest energy residual [m] | 7.6217e-13
Case: Cv valve (S1) | Largest energy residual at | L4
Case: Cv valve (S1) | Oscillating components | None
Case: Cv valve (S1) | Convergence message | converged: 10 Newton iterations in 2 outer iteration(s)
Case: Cv valve (S1) | Atmospheric pressure used [Pa(a)] | 99891.7297
Case: Cv valve (S1) | Site elevation [m] | 120
Case: Cv valve (S1) | Fluid | Water
Case: Cv valve (S1) | Fluid temperature [K] | 293.15
Case: Cv valve (S1) | Fluid concentration [mass fraction, 0–1]
Case: Cv valve (S1) | Fluid density [kg/m³] | 998.2072
Case: Cv valve (S1) | Fluid dynamic viscosity [Pa·s] | 0.0010016
Case: Cv valve (S1) | Fluid kinematic viscosity [m²/s] | 1.0034e-06
Case: Cv valve (S1) | Fluid vapor pressure [Pa(a)] | 2339.3182
Case: Cv valve (S1) | Source of the fluid's density | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Cv valve (S1) | Source of the fluid's dynamic viscosity | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
Case: Cv valve (S1) | Source of the fluid's vapor pressure | library: CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Cv valve (S1) | Lowest static pressure [Pa(g)] | 58734.4089
Case: Cv valve (S1) | Lowest static pressure at | Port 1 of Low tank_x0041_x0042_ (B)
Case: Cv valve (S1) | Highest velocity [m/s] | 2.6783
Case: Cv valve (S1) | Highest velocity in | Cooler (hot side) → -North main
Case: Cv valve (S1) | Scenario description | The PRV with a Cv 120 trim, a higher low tank and a dirty strainer.
Case: Cv valve (S1) | Scenario changes applied | 3
Case: Cv valve (S1) | Scenario changes not applied | 0
Case: Cv valve (S1) | Project link | Link 1 below reproduces this case
Case: Supply at AF1 (S2) | Status | Solved
Case: Supply at AF1 (S2) | Values in this file | Yes
Case: Supply at AF1 (S2) | Out of date | No
Case: Supply at AF1 (S2) | Solved at | 2026-10-25T12:30:00Z
Case: Supply at AF1 (S2) | Compute time [s] | 0.125
Case: Supply at AF1 (S2) | Calculation methods version | 1.4.0
Case: Supply at AF1 (S2) | Calculation methods changed | This project was last solved with calculation methods version 1.1.0. These results use version 1.4.0, so some values may differ from the ones it was shared with.
Case: Supply at AF1 (S2) | Server library: CoolProp | 8.0.0
Case: Supply at AF1 (S2) | Server library: fluids | 1.3.1
Case: Supply at AF1 (S2) | Server library: numpy | 2.5.4
Case: Supply at AF1 (S2) | Server library: opensolve-pipe | 0.1.0
Case: Supply at AF1 (S2) | Server library: scipy | 1.18.1
Case: Supply at AF1 (S2) | Converged | TRUE
Case: Supply at AF1 (S2) | Inner iterations | 10
Case: Supply at AF1 (S2) | Outer iterations | 2
Case: Supply at AF1 (S2) | Largest continuity residual [m³/s] | 2.4807e-16
Case: Supply at AF1 (S2) | Largest continuity residual at | E1:outlet
Case: Supply at AF1 (S2) | Largest energy residual [m] | 9.8854e-13
Case: Supply at AF1 (S2) | Largest energy residual at | L3
Case: Supply at AF1 (S2) | Oscillating components | None
Case: Supply at AF1 (S2) | Convergence message | converged: 10 Newton iterations in 2 outer iteration(s)
Case: Supply at AF1 (S2) | Atmospheric pressure used [Pa(a)] | 99891.7297
Case: Supply at AF1 (S2) | Site elevation [m] | 120
Case: Supply at AF1 (S2) | Fluid | Water
Case: Supply at AF1 (S2) | Fluid temperature [K] | 293.15
Case: Supply at AF1 (S2) | Fluid concentration [mass fraction, 0–1]
Case: Supply at AF1 (S2) | Fluid density [kg/m³] | 998.2072
Case: Supply at AF1 (S2) | Fluid dynamic viscosity [Pa·s] | 0.0010016
Case: Supply at AF1 (S2) | Fluid kinematic viscosity [m²/s] | 1.0034e-06
Case: Supply at AF1 (S2) | Fluid vapor pressure [Pa(a)] | 2339.3182
Case: Supply at AF1 (S2) | Source of the fluid's density | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Supply at AF1 (S2) | Source of the fluid's dynamic viscosity | library: CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
Case: Supply at AF1 (S2) | Source of the fluid's vapor pressure | library: CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
Case: Supply at AF1 (S2) | Lowest static pressure [Pa(g)] | 48945.3408
Case: Supply at AF1 (S2) | Lowest static pressure at | Port 1 of Low tank_x0041_x0042_ (B)
Case: Supply at AF1 (S2) | Highest velocity [m/s] | 2.6783
Case: Supply at AF1 (S2) | Highest velocity in | Cooler (hot side) → -North main
Case: Supply at AF1 (S2) | Scenario changes applied | 2
Case: Supply at AF1 (S2) | Scenario changes not applied | 0
Case: Supply at AF1 (S2) | Project link | Link 1 below reproduces this case
Project links | Link 1 | https://opensolve-pipe.app/p#H4sIAAAAAAACA7WYbW_aSBCA_4o1n1rJENsJ9GLpPtylnBqV9lASRepdIrSxB7yKvevurgm5iP9-ml1jAwECaitF4cX7Ms-8Dy-QyKKUAoXREP_7ApjjjBkuBcSBDzyFGK5C8CHn3yueDnGGOcSngQ-CFQgxXFdlmT97holH8KGUqj7H7qSPY9otZMEFy6_5fwhx0A0-9KOFv7oo2rHo3gddqQlLcKRQ60qhlcs8l3S5Qo1qJrkCOu1BMZFkN-6RQQR_G82NpZFaf5EpsUCimKC1NdAnZCkqz-3f4FGVGHORo3kDidbJyry90Im8m73mrJfRti1Eo6vbsJV_qaeOwrRKuJh6M5bPtsAcArIXgmyDppRcGIjDKAiC1jLLO-1rbZJSzXYhDFYAvnW0UYwLVL9GZsUMF1OIXyBFobl5hvj8_LwbBlE_Cn2Y5PLJLg99eOTCeSgh-lDWqh1KrSG2wIuGGL9XvCxQmJ2MUct4IWWOynuXSeNpnuL7w1F7wW-bF3R7_hvotGkNvSb7PHM2qhDi_jEwV9FmTug1cEP5ZPPBeB4EZ6H9H43v1Ls_3x-ZIY4J_hUZV40YnNYC__HXiov9_unbaHA1vPz6-d0dZMaUOj45wTkryhy7iSzuwL-Dj1gwkd7BMVLXeq4lZFrzqcB0bMXZpcnTVq7OV6lM5hWMi-NVVTY6sp4Z-KBwggpFsgxAniLLYUWB9eOxkCkCnZFIITAhAd3FEyWLi2WBuGyKAX09ksp908hlpRzSu5KXtZ9NuCGXc6eVvMRLkeLc0n-vmDA2_MLW74ShVIdjnTFVWpFok9ueo5iajPB8KJhBxVluJUiYepBirA1ivl0_Pugkw7TK6ZKzABb35OtyHc1WBiMbsDbbk-leq-LmlSrW8r5TR7RLHVvRwl-ENthA24c1eIW1gdQ_Cik6iigMwv5BRHXRO5CpXr2P6vR4v41av80f5NP4PBjnLhu97em2OqMa6ypNUWxuCneEx5ybnUHxE1zHX_XE4NcYzlaOFbPV6ePQEGs6Jme1s4N8kQuB6iNnBRpULlH7LWlvE7TSRhbgg5LVNBNIxZ5KSRCc9bYiudpyKNOODBo1TL0fZ-oFP8o0iI7IGNEbsfXhJxD9KJCts1tsdE_dQkVyvrg39ukT3QVNB_hQ8dzYomywKFEx4wrt-Wk37C1qzAmf09cdnNPZHZ2gYIpLDT4UaFjKDKNLEoXMIG2IgqjfCYNO1LsJgtj-_QM-pKgTxUvXJsDAnubVh8ceo9HE95g3urqll9S2KfRu2TZ7TKQe8xLbY_reEzeZZ56k1wjUJYlkyid8nxjLeSJnwnhWH15mZyNYWKBMpreotJOSDFwV5ZA_KKaenWVbBZB116luMiQAJxzzLmZeGAWeUbwgkoxPM1ReXjeSNVDKlXluKLtL77peaewuZs20I2eoFE9r30q2lgOOeeo6Sa4N9R2txZsNbYPcdM0XK11zGAULiorkdZJbHr_aJu87v__6nMGamLZ7765NIfvOO7MDyn0zGF2vDCD12M6M55LXPm25FUspbC-779oOhWHkWJbd5GWTrBuluLhuZyxeossSK4WzPjGiiL531aVgjdOFdv6sU8kLaG5wsDIFUJuoZT5D9XdZd7SUvLgV6Iv1XwuQ44OSkn69KNj80lBwu9W2BBoKIusacYid84UPleBGr42P8Dg9KSi9pE3ygoJykxtDYHhChqLgoQfQJjX7oe3b4XHENlMMXJBmMZeJu6qwZ824TmR9eTFiXQ2LxeJ_aCaO28wRAAA
Project links | Link 1 reproduces | Base case; Cv valve (S1); Supply at AF1 (S2)
Project links | Link 1: case | It opens on the base case; choose the case under Case.
Project links | Link 1: contents | It holds the whole project: every input and every scenario.
Project links | Link 1: form | Plain text: copy it into a browser.
Project links | Link 1: later versions | A link may fail to open, or solve differently, after a later change to the app; the methods version above records what produced these results.
Software | Web app version (build commit) | 0123456789abcdef0123456789abcdef01234567
Software | Web app source, at that commit | https://github.com/ccirone2/opensolve-pipe/tree/0123456789abcdef0123456789abcdef01234567
Software | Web app license | AGPL-3.0-or-later
Software | Calculation server source (for the commit it runs now) | https://api.opensolve-pipe.app/source
Disclaimer | Disclaimer | OpenSolve Pipe is an engineering aid. Its results support, but do not replace, the judgment of a qualified engineer, and are provided without warranty.

## Flags
Flags — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units — the server’s messages and the details in SI, as reported
Case id | Case | Solved at | Results | Severity | Code | Element kind | Element id | Element | Port id | Port | Pipe # | Fitting # | Message | Message (as reported, SI) | Details (SI, JSON)

## Compare cases
Compare cases — Plant water header — all cases (each case's solve and state: the Status and Solved at rows) — SI base units
Element id | Port id | Row | Quantity | Unit | Base case | Cv valve (S1) | Cv valve (S1): difference from base | Cv valve (S1): difference from base [%] | Supply at AF1 (S2) | Supply at AF1 (S2): difference from base | Supply at AF1 (S2): difference from base [%]
|  | Status | Status |  | Solved; Converged, 0 physically invalid | Solved; Converged, 0 physically invalid |  |  | Solved; Converged, 0 physically invalid
|  | Solved at | Solved at |  | 2026-10-25T12:30:00Z | 2026-10-25T12:30:00Z |  |  | 2026-10-25T12:30:00Z
PRV1 |  | Pressure-reducing valve · Flow | Flow | m³/s | 0.0075479 | 0.0069727 | -0.00057513 | -7.6197 | 0.0075479 | 0 | 0
PRV1 |  | Pressure-reducing valve · State | State |  | Active (throttling) | Active (throttling) |  |  | Active (throttling)
L4 |  | Header tee → =HYPERLINK("https://example.com","Demand") · Flow | Flow | m³/s | 0.003 | 0.003 | 1.2577e-17 | 4.1922e-13 | -0.002 | -0.005 | -166.6667
T1 | branch | Branch of Header tee · Pressure | Pressure | Pa(g) | 275862.7185 | 277441.1888 | 1578.4703 |  | 289127.719 | 13265.0005
R1 |  | Supply tank · Outflow | Outflow | m³/s | 0.015807 | 0.015232 | -0.00057513 | -3.6385 | 0.010807 | -0.005 | -31.6321
AF1 |  | =HYPERLINK("https://example.com","Demand") · Pressure | Pressure | Pa(g) | 258213.7559 | 259792.2261 | 1578.4703 |  | 285473.1769 | 27259.4211
E1 |  | Y-strainer · Flow | Flow | m³/s | 0.0075479 | 0.0069727 | -0.00057513 | -7.6197 | 0.0075479 | 0 | 0
E1 |  | Y-strainer · Pressure loss | Pressure loss | Pa | 11383.8343 | 19430.1873 | 8046.353 | 70.6823 | 11383.8343 | 0 | 0
E2 |  | Cooler (hot side) · Pressure drop | Pressure drop | Pa | 14839.7269 | 14839.7269 | 0 |  | 14839.7269 | 0
|  | Network · Lowest pressure | Lowest pressure | Pa(g) | 48945.3408 | 58734.4089 | 9789.0682 |  | 48945.3408 | 0
|  | Network · Lowest pressure (where) | Lowest pressure (where) |  | Port 1 of Low tank_x0041_x0042_ (B) | Port 1 of Low tank_x0041_x0042_ (B) |  |  | Port 1 of Low tank_x0041_x0042_ (B)
|  | Network · Highest velocity | Highest velocity | m/s | 2.6783 | 2.6783 | 0 | 0 | 2.6783 | 0 | 0
|  | Network · Highest velocity (where) | Highest velocity (where) |  | Cooler (hot side) → -North main | Cooler (hot side) → -North main |  |  | Cooler (hot side) → -North main

## Nodes
Nodes — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Component id | Component | Type | Port id | Port | Elevation [m] | Pressure [Pa(g)] | Dynamic pressure [Pa] | Total pressure [Pa(g)] | Absolute pressure [Pa(a)] | Velocity [m/s] | HGL [m] | EGL [m] | Flags
| Base case | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_1 | Port 1 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
| Base case | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_2 | Port 2 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_inlet | Run inlet | 0 | 278192.9733 | 2441.9911 | 280634.9644 | 378084.703 | 2.212 | 28.4187 | 28.6682
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_outlet | Run outlet | 0 | 279554.8691 | 1250.4408 | 280805.3099 | 379446.5988 | 1.5828 | 28.5579 | 28.6856
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | branch | Branch | 0 | 275862.7185 | 1165.1274 | 277027.8459 | 375754.4482 | 1.5279 | 28.1807 | 28.2997
| Base case | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | inlet | Inlet | 0 | 265692.5318 | 421.5371 | 266114.0689 | 365584.2615 | 0.91901 | 27.1418 | 27.1848
| Base case | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | outlet | Outlet | 0 | 120000 | 1250.4408 | 121250.4408 | 219891.7297 | 1.5828 | 12.2586 | 12.3863
| Base case | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | inlet | Inlet | 0 | 276411.1359 | 1250.4408 | 277661.5767 | 376302.8656 | 1.5828 | 28.2367 | 28.3645
| Base case | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | outlet | Outlet | 0 | 265856.2053 | 421.5371 | 266277.7424 | 365747.935 | 0.91901 | 27.1585 | 27.2015
| Base case | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | inlet | Inlet | 0 | 213976.4554 | 3580.2694 | 217556.7248 | 313868.1851 | 2.6783 | 21.8587 | 22.2245
| Base case | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | outlet | Outlet | 0.5 | 199136.7285 | 3580.2694 | 202716.9979 | 299028.4582 | 2.6783 | 20.8428 | 21.2085
| Base case | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | port_1 | Port 1 | 0 | 48945.3408 | 0 | 48945.3408 | 148837.0705 | 0 | 5 | 5
| Base case | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | Assigned flow (demand or supply) | port_1 | Port 1 | 1 | 258213.7559 | 1165.1274 | 259378.8832 | 358105.4856 | 1.5279 | 27.3778 | 27.4968
| Base case | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node (fixed pressure) | port_1 | Port 1 | 0 | 200000 | 0 | 200000 | 299891.7297 | 0 | 20.431 | 20.431
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_1 | Port 1 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_2 | Port 2 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_inlet | Run inlet | 0 | 279771.4435 | 2182.9499 | 281954.3934 | 379663.1732 | 2.0913 | 28.58 | 28.803
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_outlet | Run outlet | 0 | 281044.6379 | 1067.1404 | 282111.7783 | 380936.3676 | 1.4622 | 28.7101 | 28.8191
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | branch | Branch | 0 | 277441.1888 | 1165.1274 | 278606.3162 | 377332.9185 | 1.5279 | 28.3419 | 28.461
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | inlet | Inlet | 0 | 259470.5082 | 359.7445 | 259830.2527 | 359362.2379 | 0.84899 | 26.5061 | 26.5429
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | outlet | Outlet | 0 | 120000 | 1067.1404 | 121067.1404 | 219891.7297 | 1.4622 | 12.2586 | 12.3676
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | inlet | Inlet | 0 | 278334.6984 | 1067.1404 | 279401.8388 | 378226.4281 | 1.4622 | 28.4332 | 28.5422
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | outlet | Outlet | 0 | 259611.907 | 359.7445 | 259971.6515 | 359503.6367 | 0.84899 | 26.5206 | 26.5573
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | inlet | Inlet | 0 | 213976.4554 | 3580.2694 | 217556.7248 | 313868.1851 | 2.6783 | 21.8587 | 22.2245
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | outlet | Outlet | 0.5 | 199136.7285 | 3580.2694 | 202716.9979 | 299028.4582 | 2.6783 | 20.8428 | 21.2085
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | port_1 | Port 1 | 0 | 58734.4089 | 0 | 58734.4089 | 158626.1386 | 0 | 6 | 6
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | Assigned flow (demand or supply) | port_1 | Port 1 | 1 | 259792.2261 | 1165.1274 | 260957.3535 | 359683.9558 | 1.5279 | 27.539 | 27.658
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node (fixed pressure) | port_1 | Port 1 | 0 | 200000 | 0 | 200000 | 299891.7297 | 0 | 20.431 | 20.431
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_1 | Port 1 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | port_2 | Port 2 | 0 | 293672.0446 | 0 | 293672.0446 | 393563.7743 | 0 | 30 | 30
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_inlet | Run inlet | 0 | 289119.8128 | 675.5641 | 289795.3769 | 389011.5425 | 1.1634 | 29.535 | 29.604
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | run_outlet | Run outlet | 0 | 288119.1608 | 1250.4408 | 289369.6016 | 388010.8905 | 1.5828 | 29.4327 | 29.5605
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | branch | Branch | 0 | 289127.719 | 517.8344 | 289645.5534 | 389019.4487 | 1.0186 | 29.5358 | 29.5887
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | inlet | Inlet | 0 | 274256.8235 | 421.5371 | 274678.3606 | 374148.5532 | 0.91901 | 28.0166 | 28.0597
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | Pressure-reducing valve (PRV) | outlet | Outlet | 0 | 120000 | 1250.4408 | 121250.4408 | 219891.7297 | 1.5828 | 12.2586 | 12.3863
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | inlet | Inlet | 0 | 284975.4276 | 1250.4408 | 286225.8684 | 384867.1573 | 1.5828 | 29.1116 | 29.2393
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | Equipment (rated pressure drop) | outlet | Outlet | 0 | 274420.497 | 421.5371 | 274842.0341 | 374312.2267 | 0.91901 | 28.0334 | 28.0764
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | inlet | Inlet | 0 | 213976.4554 | 3580.2694 | 217556.7248 | 313868.1851 | 2.6783 | 21.8587 | 22.2245
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | Equipment (rated pressure drop) | outlet | Outlet | 0.5 | 199136.7285 | 3580.2694 | 202716.9979 | 299028.4582 | 2.6783 | 20.8428 | 21.2085
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | port_1 | Port 1 | 0 | 48945.3408 | 0 | 48945.3408 | 148837.0705 | 0 | 5 | 5
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | Assigned flow (demand or supply) | port_1 | Port 1 | 1 | 285473.1769 | 517.8344 | 285991.0113 | 385364.9067 | 1.0186 | 30.1624 | 30.2153
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node (fixed pressure) | port_1 | Port 1 | 0 | 200000 | 0 | 200000 | 299891.7297 | 0 | 20.431 | 20.431

## Links
Links — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Connection id | Connection | From id | From port | To id | To port | Flow (+ from → to) [m³/s] | Largest velocity [m/s] | Head loss (EGL from − to) [m] | Friction loss (+ with the flow) [m] | Fittings loss (+ with the flow) [m] | Pipes | Fittings | Flags
| Base case | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | R1 | port_1 | T1 | run_inlet | 0.010548 | 2.212 | 1.3318 | 1.2071 | 0.12473 | 1 | 1
| Base case | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | T1 | run_outlet | E1 | inlet | 0.0075479 | 1.5828 | 0.32115 | 0.32115 | 0 | 1 | 0
| Base case | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | E1 | outlet | PRV1 | inlet | 0.0075479 | 0.91901 | 0.01672 | 0.01672 | 0 | 1 | 0
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | PRV1 | outlet | R2 | port_1 | 0.0075479 | 1.5828 | 7.3863 | 7.2589 | 0.12736 | 2 | 3
| Base case | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | T1 | branch | AF1 | port_1 | 0.003 | 1.5279 | 0.80293 | 0.80293 | 0 | 1 | 0
| Base case | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | R1 | port_2 | E2 | inlet | 0.0052589 | 2.6783 | 7.7755 | 7.7755 | 0 | 1 | 0
| Base case | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | E2 | outlet | R3 | port_1 | 0.0052589 | 2.6783 | 0.77755 | 0.77755 | 0 | 1 | 0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | R1 | port_1 | T1 | run_inlet | 0.0099727 | 2.0913 | 1.197 | 1.0855 | 0.1115 | 1 | 1
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | T1 | run_outlet | E1 | inlet | 0.0069727 | 1.4622 | 0.27683 | 0.27683 | 0 | 1 | 0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | E1 | outlet | PRV1 | inlet | 0.0069727 | 0.84899 | 0.014445 | 0.014445 | 0 | 1 | 0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | PRV1 | outlet | R2 | port_1 | 0.0069727 | 1.4622 | 6.3676 | 6.2589 | 0.10869 | 2 | 3
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | T1 | branch | AF1 | port_1 | 0.003 | 1.5279 | 0.80293 | 0.80293 | 0 | 1 | 0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | R1 | port_2 | E2 | inlet | 0.0052589 | 2.6783 | 7.7755 | 7.7755 | 0 | 1 | 0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | E2 | outlet | R3 | port_1 | 0.0052589 | 2.6783 | 0.77755 | 0.77755 | 0 | 1 | 0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | R1 | port_1 | T1 | run_inlet | 0.0055479 | 1.1634 | 0.39602 | 0.36151 | 0.034506 | 1 | 1
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | T1 | run_outlet | E1 | inlet | 0.0075479 | 1.5828 | 0.32115 | 0.32115 | 0 | 1 | 0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | E1 | outlet | PRV1 | inlet | 0.0075479 | 0.91901 | 0.01672 | 0.01672 | 0 | 1 | 0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | PRV1 | outlet | R2 | port_1 | 0.0075479 | 1.5828 | 7.3863 | 7.2589 | 0.12736 | 2 | 3
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | T1 | branch | AF1 | port_1 | -0.002 | 1.0186 | -0.62667 | -0.62667 | 0 | 1 | 0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | R1 | port_2 | E2 | inlet | 0.0052589 | 2.6783 | 7.7755 | 7.7755 | 0 | 1 | 0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | E2 | outlet | R3 | port_1 | 0.0052589 | 2.6783 | 0.77755 | 0.77755 | 0 | 1 | 0

## Pipes
Pipes — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Connection id | Connection | Pipe # | Material | Schedule | Nominal size | Inner diameter [m] | Length [m] | Roughness [m] | Velocity (signed as the flow) [m/s] | Re | f (Darcy) | Regime | Friction loss (+ with the flow) [m] | Flags
| Base case | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 20 | 3.5116e-05 | 2.212 | 171772.5169 | 0.018852 | Turbulent | 1.2071
| Base case | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 10 | 3.5116e-05 | 1.5828 | 122917.3544 | 0.01959 | Turbulent | 0.32115
| Base case | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | 1 | Carbon steel | 40 | NPS 4 | 0.10226 | 2 | 3.501e-05 | 0.91901 | 93660.4758 | 0.019853 | Turbulent | 0.01672
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 200 | 3.5116e-05 | 1.5828 | 122917.3544 | 0.01959 | Turbulent | 6.4229
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | Carbon steel | 40 | NPS 4 | 0.10226 | 100 | 3.501e-05 | 0.91901 | 93660.4758 | 0.019853 | Turbulent | 0.836
| Base case | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | 1 | Custom pipe |  |  | 0.05 | 15 | 4.5e-05 | 1.5279 | 76135.8853 | 0.022487 | Turbulent | 0.80293
| Base case | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | 1 | Custom pipe |  |  | 0.05 | 50 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 7.7755
| Base case | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | 1 | Custom pipe |  |  | 0.05 | 5 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 0.77755
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 20 | 3.5116e-05 | 2.0913 | 162406.5426 | 0.018965 | Turbulent | 1.0855
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 10 | 3.5116e-05 | 1.4622 | 113551.38 | 0.019787 | Turbulent | 0.27683
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | 1 | Carbon steel | 40 | NPS 4 | 0.10226 | 2 | 3.501e-05 | 0.84899 | 86523.7975 | 0.020097 | Turbulent | 0.014445
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 200 | 3.5116e-05 | 1.4622 | 113551.38 | 0.019787 | Turbulent | 5.5367
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | Carbon steel | 40 | NPS 4 | 0.10226 | 100 | 3.501e-05 | 0.84899 | 86523.7975 | 0.020097 | Turbulent | 0.72223
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | 1 | Custom pipe |  |  | 0.05 | 15 | 4.5e-05 | 1.5279 | 76135.8853 | 0.022487 | Turbulent | 0.80293
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | 1 | Custom pipe |  |  | 0.05 | 50 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 7.7755
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | 1 | Custom pipe |  |  | 0.05 | 5 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 0.77755
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 20 | 3.5116e-05 | 1.1634 | 90347.246 | 0.020409 | Turbulent | 0.36151
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L2 | Header tee → Y-strainer | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 10 | 3.5116e-05 | 1.5828 | 122917.3544 | 0.01959 | Turbulent | 0.32115
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L6 | Y-strainer → Pressure-reducing valve | 1 | Carbon steel | 40 | NPS 4 | 0.10226 | 2 | 3.501e-05 | 0.91901 | 93660.4758 | 0.019853 | Turbulent | 0.01672
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | Carbon steel | 40 | NPS 3 | 0.07792 | 200 | 3.5116e-05 | 1.5828 | 122917.3544 | 0.01959 | Turbulent | 6.4229
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | Carbon steel | 40 | NPS 4 | 0.10226 | 100 | 3.501e-05 | 0.91901 | 93660.4758 | 0.019853 | Turbulent | 0.836
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L4 | Header tee → =HYPERLINK("https://example.com","Demand") | 1 | Custom pipe |  |  | 0.05 | 25 | 4.5e-05 | -1.0186 | 50757.2569 | 0.023693 | Turbulent | -0.62667
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L5 | Supply tank → Cooler (hot side) | 1 | Custom pipe |  |  | 0.05 | 50 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 7.7755
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L7 | Cooler (hot side) → -North main | 1 | Custom pipe |  |  | 0.05 | 5 | 4.5e-05 | 2.6783 | 133462.8979 | 0.02126 | Turbulent | 0.77755

## Fittings
Fittings — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Connection id | Connection | Fitting # | Type id | Fitting | Pipe # | Quantity | K (each) | K referred to diameter [m] | Head loss, all (+ with the flow) [m] | K source | Flags
| Base case | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | entrance_sharp | Pipe entrance, sharp-edged (flush) | 1 | 1 | 0.5 | 0.07792 | 0.12473 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.entrance_sharp(method='Crane')
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | elbow_90_lr | 90° elbow, long radius (r/D = 1.5), welded or flanged | 1 | 2 | 0.24203 | 0.07792 | 0.061833 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.bend_rounded_Crane (K = Crane multiplier x ft_Crane(Di), Chebyshev fit to the Crane r/D table)
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | reducer_sudden | Sudden reducer (contraction or expansion by flow direction) | 1 | 1 | 0.17589 | 0.07792 | 0.022467 | Expansion: Rennels & Hudson, Pipe Flow (Wiley, 2012), K = (1 - beta^2)^2 on the smaller upstream pipe, via fluids 1.3.1 fluids.fittings.diffuser_sharp. Contraction: Crane Co. TP-410 (2009), K on the smaller downstream pipe, via fluids 1.3.1 fluids.fittings.contraction_sharp(method='Crane')
| Base case | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 3 | exit | Pipe exit into a large body of liquid | 2 | 1 | 1 | 0.10226 | 0.043062 | Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012; via fluids 1.3.1 fluids.fittings.exit_normal
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | entrance_sharp | Pipe entrance, sharp-edged (flush) | 1 | 1 | 0.5 | 0.07792 | 0.1115 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.entrance_sharp(method='Crane')
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | elbow_90_lr | 90° elbow, long radius (r/D = 1.5), welded or flanged | 1 | 2 | 0.24203 | 0.07792 | 0.052769 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.bend_rounded_Crane (K = Crane multiplier x ft_Crane(Di), Chebyshev fit to the Crane r/D table)
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | reducer_sudden | Sudden reducer (contraction or expansion by flow direction) | 1 | 1 | 0.17589 | 0.07792 | 0.019174 | Expansion: Rennels & Hudson, Pipe Flow (Wiley, 2012), K = (1 - beta^2)^2 on the smaller upstream pipe, via fluids 1.3.1 fluids.fittings.diffuser_sharp. Contraction: Crane Co. TP-410 (2009), K on the smaller downstream pipe, via fluids 1.3.1 fluids.fittings.contraction_sharp(method='Crane')
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 3 | exit | Pipe exit into a large body of liquid | 2 | 1 | 1 | 0.10226 | 0.03675 | Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012; via fluids 1.3.1 fluids.fittings.exit_normal
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L1 | Supply tank → Header tee | 1 | entrance_sharp | Pipe entrance, sharp-edged (flush) | 1 | 1 | 0.5 | 0.07792 | 0.034506 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.entrance_sharp(method='Crane')
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 1 | elbow_90_lr | 90° elbow, long radius (r/D = 1.5), welded or flanged | 1 | 2 | 0.24203 | 0.07792 | 0.061833 | Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe (2009), via fluids 1.3.1 fluids.fittings.bend_rounded_Crane (K = Crane multiplier x ft_Crane(Di), Chebyshev fit to the Crane r/D table)
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 2 | reducer_sudden | Sudden reducer (contraction or expansion by flow direction) | 1 | 1 | 0.17589 | 0.07792 | 0.022467 | Expansion: Rennels & Hudson, Pipe Flow (Wiley, 2012), K = (1 - beta^2)^2 on the smaller upstream pipe, via fluids 1.3.1 fluids.fittings.diffuser_sharp. Contraction: Crane Co. TP-410 (2009), K on the smaller downstream pipe, via fluids 1.3.1 fluids.fittings.contraction_sharp(method='Crane')
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | L3 | Pressure-reducing valve → Low tank_x0041_x0042_ (B) | 3 | exit | Pipe exit into a large body of liquid | 2 | 1 | 1 | 0.10226 | 0.043062 | Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012; via fluids 1.3.1 fluids.fittings.exit_normal

## Valves
Valves — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Valve id | Valve | Type | State | Flow (+ inlet → outlet) [m³/s] | Head loss [m] | Pressure drop, static [Pa] | K (open) | K referred to diameter [m] | K effective | Cv effective | Pressure setpoint [Pa(g)] | Flow setpoint [m³/s] | Setpoint achieved | Flags
| Base case | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | PRV | Active (throttling) | 0.0075479 | 14.7985 | 145692.5318 | 0 | 0.10226 | 343.6557 | 26.0858 | 120000 |  | TRUE
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | PRV | Active (throttling) | 0.0069727 | 14.1753 | 139470.5082 | 16.2394 | 0.10226 | 385.7268 | 24.6222 | 120000 |  | TRUE
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | PRV1 | Pressure-reducing valve | PRV | Active (throttling) | 0.0075479 | 15.6734 | 154256.8235 | 0 | 0.10226 | 363.9726 | 25.3473 | 120000 |  | TRUE

## Equipment
Equipment — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Equipment id | Equipment | Flow (+ inlet → outlet) [m³/s] | Flow ÷ rated flow | Pressure loss [Pa] | Head loss [m] | Pressure drop, static [Pa] | Rated by | Rated pressure drop (loss) [Pa] | Rated flow [m³/s] | Rated fluid density [kg/m³] | Flow coefficient | Flags
| Base case | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | 0.0075479 | 0.75479 | 11383.8343 | 1.1629 | 10554.9306 | Pressure drop at a flow | 20000 | 0.01 | 999.1026
| Base case | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | 0.0052589 |  | 9945.1928 | 1.0159 | 14839.7269 | Kv |  |  |  | 60
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | 0.0069727 | 0.69727 | 19430.1873 | 1.9849 | 18722.7914 | Pressure drop at a flow | 40000 | 0.01 | 999.1026
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | 0.0052589 |  | 9945.1928 | 1.0159 | 14839.7269 | Kv |  |  |  | 60
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E1 | Y-strainer | 0.0075479 | 0.75479 | 11383.8343 | 1.1629 | 10554.9306 | Pressure drop at a flow | 20000 | 0.01 | 999.1026
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | E2 | Cooler (hot side) | 0.0052589 |  | 9945.1928 | 1.0159 | 14839.7269 | Kv |  |  |  | 60

## Branches
Branches — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Branch id | Branch | Type | Loss model | Flow pattern | Combined port id | Combined-flow velocity [m/s] | K is on | Correlation | In correlation range | Flags
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | Crane TP-410 (flow-split dependent K) | Diverging from run inlet | run_inlet | 2.212 | Combined-flow velocity | Crane Co. TP-410 (2009) via fluids 1.3.1 fluids.fittings.K_branch_diverging_Crane, K_run_diverging_Crane (D_run = 0.07792 m, D_branch = 0.05 m, angle 90°); K on the combined-flow velocity in D_run | TRUE
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | Crane TP-410 (flow-split dependent K) | Diverging from run inlet | run_inlet | 2.0913 | Combined-flow velocity | Crane Co. TP-410 (2009) via fluids 1.3.1 fluids.fittings.K_branch_diverging_Crane, K_run_diverging_Crane (D_run = 0.07792 m, D_branch = 0.05 m, angle 90°); K on the combined-flow velocity in D_run | TRUE
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | Tee | Crane TP-410 (flow-split dependent K) | Converging to run outlet | run_outlet | 1.5828 | Combined-flow velocity | Crane Co. TP-410 (2009) via fluids 1.3.1 fluids.fittings.K_branch_converging_Crane, K_run_converging_Crane (D_run = 0.07792 m, D_branch = 0.05 m, angle 90°); K on the combined-flow velocity in D_run | TRUE

## Branch ports
Branch ports — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Branch id | Branch | Port id | Port | Flow (+ into the branch) [m³/s] | Combined port | K of the path from the combined port | Velocity K is on [m/s] | Path head loss (+ in the flow direction) [m]
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_inlet | Run inlet | 0.010548 | TRUE
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_outlet | Run outlet | -0.0075479 | FALSE | -0.069757 | 2.212 | -0.017402
| Base case | 2026-10-25T12:30:00Z | Current | T1 | Header tee | branch | Branch | -0.003 | FALSE | 1.4771 | 2.212 | 0.36848
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_inlet | Run inlet | 0.0099727 | TRUE
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_outlet | Run outlet | -0.0069727 | FALSE | -0.072097 | 2.0913 | -0.016078
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | T1 | Header tee | branch | Branch | -0.003 | FALSE | 1.5337 | 2.0913 | 0.34202
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_inlet | Run inlet | 0.0055479 | FALSE | 0.3405 | 1.5828 | 0.043495
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | run_outlet | Run outlet | -0.0075479 | TRUE
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | T1 | Header tee | branch | Branch | 0.002 | FALSE | 0.22068 | 1.5828 | 0.02819

## Boundaries
Boundaries — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Boundary id | Boundary | Type | EGL [m] | Net outflow (+ into the network) [m³/s] | Ports | Flags
| Base case | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | 30 | 0.015807 | 2
| Base case | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | 5 | -0.0075479 | 1
| Base case | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node | 20.431 | -0.0052589 | 1
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | 30 | 0.015232 | 2
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | 6 | -0.0069727 | 1
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node | 20.431 | -0.0052589 | 1
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | Reservoir | 30 | 0.010807 | 2
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R2 | Low tank_x0041_x0042_ (B) | Reservoir | 5 | -0.0075479 | 1
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R3 | -North main | Reference node | 20.431 | -0.0052589 | 1

## Boundary ports
Boundary ports — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Boundary id | Boundary | Port id | Port | Outflow (+ into the network) [m³/s]
| Base case | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_1 | Port 1 | 0.010548
| Base case | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_2 | Port 2 | 0.0052589
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_1 | Port 1 | 0.0099727
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_2 | Port 2 | 0.0052589
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_1 | Port 1 | 0.0055479
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | R1 | Supply tank | port_2 | Port 2 | 0.0052589

## Assigned flows
Assigned flows — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Node id | Node | Port id | Direction | Assigned flow (+ demand, − supply) [m³/s] | Net outflow (+ into the network) [m³/s] | Elevation [m] | Pressure [Pa(g)] | Absolute pressure [Pa(a)] | HGL [m] | Flags
| Base case | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | port_1 | Demand | 0.003 | -0.003 | 1 | 258213.7559 | 358105.4856 | 27.3778
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | port_1 | Demand | 0.003 | -0.003 | 1 | 259792.2261 | 359683.9558 | 27.539
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | AF1 | =HYPERLINK("https://example.com","Demand") | port_1 | Supply | -0.002 | 0.002 | 1 | 285473.1769 | 385364.9067 | 30.1624

## Scenario changes
Scenario changes — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units
Case id | Case | Solved at | Results | Change # | Target | Element id | Pipe # | Field | Field id | State | Value | Base value | Unit | Value (SI, JSON) | Base value (SI, JSON) | SI unit | Message
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | 1 | Pressure-reducing valve | PRV1 |  | Resistance | resistance | Applied | Cv 120 | Default |  | {"kind":"Cv","value":120} | null
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | 2 | Low tank_x0041_x0042_ (B) | R2 |  | Liquid level | liquidLevel | Applied | 6 | 5 | m | 6 | 5 | m
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | 3 | Y-strainer | E1 |  | Rated pressure drop | rating.pressureLoss | Applied | 40000 | 20000 | Pa | 40000 | 20000 | Pa (difference)
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | 1 | =HYPERLINK("https://example.com","Demand") | AF1 |  | Assigned flow | flow | Applied | -0.002 | 0.003 | m³/s | -0.002 | 0.003 | m³/s
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | 2 | Pipe 1 of Header tee → =HYPERLINK("https://example.com","Demand") | L4 | 1 | Length | length | Applied | 25 | 15 | m | 25 | 15 | m

## Methods
Methods — Plant water header — all cases (each row's case and solve: Case, Solved at, Results) — SI base units — SI, as reported
Case id | Case | Solved at | Results | Text
| Base case | 2026-10-25T12:30:00Z | Current | Calculation methods and assumptions
| Base case | 2026-10-25T12:30:00Z | Current | Project: Plant water header
| Base case | 2026-10-25T12:30:00Z | Current | Case: base case
| Base case | 2026-10-25T12:30:00Z | Current | OpenSolve Pipe calculation methods version 1.4.0
| Base case | 2026-10-25T12:30:00Z | Current | Solved: 2026-10-25T12:30:00Z
| Base case | 2026-10-25T12:30:00Z | Current | Solve status: converged.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Network solution
| Base case | 2026-10-25T12:30:00Z | Current | - Global Gradient Algorithm (Todini & Pilati 1988): Newton's method on the energy grade line at every node and the flow in every link; sparse direct solve of the Schur complement (SciPy SuperLU, splu). One solver for every topology; every connected part needs a reservoir or reference node.
| Base case | 2026-10-25T12:30:00Z | Current | - Converged when the largest flow change is at most the project tolerance times the largest flow (plus 1e-14 m³/s), continuity closes at every node and over every component to 1e-09 x the largest flow + 1e-14 m³/s, and the energy equation holds on every link to 1e-07 m. On each link, 8.88178e-16 x the largest magnitude among the energy grade lines at its two ends and its head loss is added to that tolerance (4 x 2.22045e-16, the machine epsilon of double precision): an allowance for the round-off of the heads that the energy residual subtracts, larger than 1e-07 m only where that magnitude exceeds 1e-07 m divided by that factor, about 1.1259e+08 m.
| Base case | 2026-10-25T12:30:00Z | Current | - An active PRV or PSV holds its port's head and passes the flow of the pipe on that port, coupled exactly in Newton's step (EPANET 2.2 lags it by one iteration, which converges the same answer more slowly).
| Base case | 2026-10-25T12:30:00Z | Current | - This project: friction method 'colebrook', flow tolerance 1e-09 (relative to the largest flow), at most 100 Newton iterations per network solve.
| Base case | 2026-10-25T12:30:00Z | Current | - This solve: 10 Newton iterations in 2 outer iteration(s); converged.
| Base case | 2026-10-25T12:30:00Z | Current | - Branch components (tees, wyes) are imposed exactly: each one's ports share one head unknown, offset by the branch's path losses (zero for an ideal junction), and its internal flows follow from continuity.
| Base case | 2026-10-25T12:30:00Z | Current | - Flows below 1e-12 x the largest flow (plus 1e-14 m³/s) are round-off and reported as zero. Dead-end branches (no way out but the node they hang from) carry no flow by continuity and are reported as exactly zero.
| Base case | 2026-10-25T12:30:00Z | Current | - Outer loop for statuses and branch losses: at most 30 counted iterations; an iteration that only holds or releases branch legs at zero flow is not counted (each branch is held a bounded number of times). Once pump and valve statuses repeat after an iteration that changed several of them, one status changes per iteration; a status pattern that still repeats goes back to the latest iteration that asked for several changes and takes one not yet taken, and with none left is reported as not converged, naming the elements that oscillate.
| Base case | 2026-10-25T12:30:00Z | Current | - Parts of the network closed off from every reservoir and reference node by closed elements carry no flow and have no computed pressure (flagged).
| Base case | 2026-10-25T12:30:00Z | Current | - A closed-off part that cannot carry zero flow (a pump loop behind a closed valve) has determined flows but no pressure level: its flows and head differences are solved with one node held at an arbitrary head, and its pressures, NPSH available and PRV/PSV setpoint checks are not reported (flagged).
| Base case | 2026-10-25T12:30:00Z | Current | - Assigned-flow nodes fix the flow leaving the network at their port (a demand, positive) or entering it (a supply, negative), whatever the pressure there: a nodal demand in the continuity equations, as EPANET's junction demands; their pressure is a result. They are not a fixed-pressure boundary. A dead-end branch to one carries its flow. A part of the network that no reservoir or reference node reaches through open elements carries assigned flows only if they sum to zero (to the continuity tolerance): its flows are then solved and its pressure level is not (flagged); otherwise the closed elements around that part whose status rules open as its pressure falls (a net demand) or rises (a net supply) are re-opened; with none left to open, no steady state carries them, and the solve is reported as not converged, naming the nodes and the elements closed around them (EPANET: a disconnected system). A flow control (an FCV, or a speed-controlled pump) that alone feeds assigned-flow nodes taking its setpoint flow leaves the pressure between them undetermined (reported as not converged, naming them); with another flow the node's flow passes and the control's rules take it to a limit (an FCV fully open below its setpoint, a speed-controlled pump at its maximum or minimum speed), or, above what the control can pass, or with reverse flow through it, no steady state carries it.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Todini, E., and S. Pilati. A gradient algorithm for the analysis of pipe networks. Computer Applications in Water Supply, Vol. 1. Wiley, 1988, 1-20.
| Base case | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Pipe friction
| Base case | 2026-10-25T12:30:00Z | Current | - Darcy–Weisbach head loss h = f (L/D) v²/(2g), g = 9.80665 m/s² (standard gravity, fluids.constants.g), Re = ¦v¦ D/ν.
| Base case | 2026-10-25T12:30:00Z | Current | - Laminar, Re < 2000: f = 64/Re (Hagen–Poiseuille).
| Base case | 2026-10-25T12:30:00Z | Current | - Turbulent, Re ≥ 4000: the Colebrook (1939) equation, solved exactly with fluids.friction.Clamond (Clamond 2009).
| Base case | 2026-10-25T12:30:00Z | Current | - Transition, 2000 ≤ Re < 4000: cubic interpolation between the laminar and turbulent laws (Dunlop's method, as in EPANET 2.2); flagged as transitional flow.
| Base case | 2026-10-25T12:30:00Z | Current | - Flagged outside the cited range: Swamee–Jain beyond its documented 5000 ≤ Re ≤ 1e+08 and 1e-06 ≤ ε/D ≤ 0.05; Colebrook beyond ε/D = 0.05, the largest relative roughness documented for its explicit approximations (fluids.friction.fmethods). ε/D ≥ 3.7 has no Colebrook solution and is rejected.
| Base case | 2026-10-25T12:30:00Z | Current | - Pipe dimensions: ASME B36.10M / B36.19M and ASTM D1785 via fluids.piping; roughness: Farshad & Rieke (2006) via fluids.friction.roughness_Farshad; user values where entered (each element's trace names its sources).
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Colebrook, C. F. J. ICE 11(4), 1939, 133-156, doi:10.1680/ijoti.1939.13150.
| Base case | 2026-10-25T12:30:00Z | Current | - Clamond, D. Ind. Eng. Chem. Res. 48(7), 2009, 3665-3671, doi:10.1021/ie801626g.
| Base case | 2026-10-25T12:30:00Z | Current | - Swamee, P. K., and A. K. Jain. J. Hydraulics Div. ASCE 102(5), 1976, 657-664.
| Base case | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Minor losses
| Base case | 2026-10-25T12:30:00Z | Current | - Fitting loss h = n K v²/(2g), K from the cited fluids correlation for the fitting type (data/fittings.json) at the reference pipe's inner diameter; a user K overrides it.
| Base case | 2026-10-25T12:30:00Z | Current | - Crane TP-410 K values use the fully turbulent friction factor ft_Crane(D); they are not valid in laminar flow, and a Crane K in a laminar segment is flagged.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
| Base case | 2026-10-25T12:30:00Z | Current | - Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Branches
| Base case | 2026-10-25T12:30:00Z | Current | - Tees and wyes with lossModel 'ideal' are junctions without loss, as in EPANET.
| Base case | 2026-10-25T12:30:00Z | Current | - lossModel 'crane': the path losses follow the solved flow split with the Crane TP-410 tee and lateral correlations (fluids.fittings.K_branch_diverging_Crane, K_run_diverging_Crane, K_branch_converging_Crane, K_run_converging_Crane), K on the combined-flow velocity in the run diameter; updated in the outer loop until K changes by less than 0.0001 and the path loss by less than 1e-06 m.
| Base case | 2026-10-25T12:30:00Z | Current | - A tee whose combined flow passes through the branch uses the Darby 3-K tee 'Tee, Through-branch, (as elbow), flanged, (r/D = 1)' per run path on its own velocity (flagged); a wye in that pattern has no cited correlation and is reported as not converged.
| Base case | 2026-10-25T12:30:00Z | Current | - Flagged outside the correlations' range: a branch larger than the run (β > 1), unequal run pipes, a wye lateral turning against its lean, and a laminar combined flow (Re < 2000 on the combined-flow velocity in the run diameter: the Crane tee data are for turbulent flow).
| Base case | 2026-10-25T12:30:00Z | Current | - Zero flow through a leg: the correlations for flow out through a leg and flow in through it give different port heads in the limit of zero flow. A leg whose flow reverses and reverses back between outer iterations is held at zero flow while the head the network gives its port lies between those two limits; its K is the one its head implies.
| Base case | 2026-10-25T12:30:00Z | Current | - A flow split that keeps alternating across a step of a Crane correlation (a split at which the fluids function switches formula, q = 0.4, 0.5 or 0.6, and K jumps by more than 0.0001) holds K at the mean of the fluids values at the two splits while the solved split stays between them (flagged; the trace lists both values); a split alternating where the correlation is continuous has its K update under-relaxed instead.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
| Base case | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Pumps
| Base case | 2026-10-25T12:30:00Z | Current | - Head, efficiency and NPSHr curves: monotone piecewise cubic interpolation (SciPy PchipInterpolator) through the entered points; head and NPSHr are extrapolated along the end slope outside the points (flagged), efficiency is held at its end values (flagged).
| Base case | 2026-10-25T12:30:00Z | Current | - Speed: affinity laws, H(Q) = s² H₀(Q/s), NPSHr(Q) = s² NPSHr₀(Q/s), η(Q) = η₀(Q/s).
| Base case | 2026-10-25T12:30:00Z | Current | - No viscosity correction: the curves are used as entered for the fluid (the Hydraulic Institute correction, ANSI/HI 9.6.7, is not in this version).
| Base case | 2026-10-25T12:30:00Z | Current | - Integral check: a pump closes when the system head exceeds its shutoff head s² H₀(0) or the flow would reverse (EPANET 2.2 pumpstatus), and is flagged as flow reversal.
| Base case | 2026-10-25T12:30:00Z | Current | - System curve of a pump: at each flow the pump is replaced by that fixed flow and the network solved, every other element following its own law and status rules (other pumps keep running); the system head is EGL(discharge) − EGL(suction). Default flows: 0 to 1.2 x the curve's largest flow x s. Each point starts from the solution at the neighbouring flow (statuses, branch losses and flows; the first from the network's own solve when the solve computes the curves, from the initial state otherwise), so where the statuses or branch patterns admit more than one solution the curve follows one continuously; a point that fails from there is solved from the initial state, and one that still has no head while the flow has a way through (unless a control valve in series is at its switch, below) is solved again from the initial state (if it did not start there) and from it with its active control valves open, the first solve that gives a head, or finds a control valve in series at its switch, being used (with none, the point keeps its first result) and the next point starting from the result used; a flowing point is not solved again when its flow exceeds what every way from the pump's discharge back to its suction can pass that way (an FCV at most its setpoint, a check valve, PRV, PSV or pump nothing in reverse: a cut, Ford and Fulkerson), since no steady state carries it, and one whose flow is that limit, where every steady state passes each FCV of the cut at its setpoint, is also solved with each such FCV held open, to find whether it sits at its switch. A point has no head where no steady state carries its flow, where its head is undetermined (a side of the pump with no fixed pressure, or a control valve in series at its switch, which could also hold the flow throttled with any higher head) or where its solve does not converge; its message says which. With assigned-flow nodes, the cut counts their flows as fixed demands and supplies (Gale): a demand on the pump's side of the cut takes part of the forced flow, and one beyond it adds to what the cut must pass. Read the other way, the cut bounds the flow from below: a flowing point below the least flow that assigned flows need through the pump (a demand on its discharge side that a one-way element keeps every reservoir and reference node from feeding, or a supply on its suction side that one keeps from draining) has no steady state either and is not solved again, and one at that floor is solved with each FCV of the cut held open too. A side of the pump that reaches only assigned-flow nodes has no point with a head.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and R. E. Carlson. Monotone piecewise cubic interpolation. SIAM J. Numer. Anal. 17(2), 1980, 238-246.
| Base case | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and J. Butland. A method for constructing local monotone piecewise cubic interpolants. SIAM J. Sci. Stat. Comput. 5(2), 1984, 300-304, doi:10.1137/0905021 (the derivative formula of scipy.interpolate.PchipInterpolator).
| Base case | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
| Base case | 2026-10-25T12:30:00Z | Current | - Ford, L. R., and D. R. Fulkerson. Maximal flow through a network. Canadian Journal of Mathematics 8, 1956, 399-404 (the max-flow min-cut theorem: the flows no state carries through a pump on its system curve).
| Base case | 2026-10-25T12:30:00Z | Current | - Gale, D. A theorem on flows in networks. Pacific Journal of Mathematics 7(2), 1957, 1073-1082 (a flow with fixed supplies and demands exists when no node set holds more net supply than its cut can pass: the assigned flows in a pump's system-curve bounds).
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Valves
| Base case | 2026-10-25T12:30:00Z | Current | - Open valve loss h = K v²/(2g) on the inlet pipe's inner diameter; Cv and Kv converted with fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01, turbulent flow, without the Reynolds number factor F_R); without a resistance, the Crane TP-410 full-bore K for the valve type. A Cv, Kv or Crane K in laminar flow (Re < 2000 in the inlet pipe) is flagged.
| Base case | 2026-10-25T12:30:00Z | Current | - Active check valves: open loss h = Δp_crack/(ρg) + K v²/(2g); open above their cracking head and close on reverse flow (EPANET 2.2 cvstatus with the cracking head). A check valve locked open by the user has the open loss K v²/(2g) only, with no cracking head and no check action; locked closed, it passes no flow.
| Base case | 2026-10-25T12:30:00Z | Current | - PRV, PSV and FCV hold the outlet static pressure, inlet static pressure or flow when active; status rules from EPANET 2.2 (hydstatus.c) applied to the energy grade line, with the setpoint head z + p/(ρg) + v²/(2g) at the port; an FCV closes on reverse flow (EPANET's would pass it), and an active FCV opens once the head across it is below its fully open loss at the setpoint (EPANET's waits for a reverse head), as the PRV and PSV rules do. Control valves without a resistance: ideal control valve: no loss when fully open (K = 0); give a resistance for a real valve.
| Base case | 2026-10-25T12:30:00Z | Current | - Status tolerances: 0.0001 m in head, 1e-08 m³/s in flow.
| Base case | 2026-10-25T12:30:00Z | Current | - An active state with no solution falls back to the states the valve rules give at that solve's first iterations (EPANET 2.2 applies them at every iteration), then to open and closed valves (EPANET's badvalve).
| Base case | 2026-10-25T12:30:00Z | Current | - A section closed off by closed pumps or valves carries no flow and has no computed pressure; the closed elements around it are re-tested against the heads it can take at zero flow (a dead-headed pump puts its shutoff head on it), and re-opened when no such head keeps them all closed. A PRV or PSV inside such a section or one whose pressure level is undetermined, or closed between two of them, keeps its state only if one set of section levels holds it together with those closed elements and the other such valves; otherwise the fewest of these elements change, each to the state its rule gives at levels that hold the others (a PRV or PSV that could not be active there, with no fixed head to draw from or deliver to, closes if open and opens if closed).
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
| Base case | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
| Base case | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Equipment
| Base case | 2026-10-25T12:30:00Z | Current | - Equipment (one side of a heat exchanger, a coil, a strainer, a filter, or another passive element given by its datasheet): the loss of total head from its inlet to its outlet is h = EGL_in − EGL_out = c Q¦Q¦ (a loss of total pressure ρ g h), with c = ΔP_r/(ρ_r g Q_r²) from the rated pressure drop ΔP_r at the rated flow Q_r for a fluid of density ρ_r: a constant K, the square law of ISA-75.01.01-2007 eq. (1) for non-choked, turbulent liquid flow, and the high-Re limit of the 3-K method (Silverberg & Darby). The rated drop is the dissipative loss (friction and form) of total pressure between the ports, without the static head between them: each port's static pressure follows from its EGL with the velocity in its connected pipe, so the static drop reported is ρ g h + ρ g (z_out − z_in) + ρ (v_out² − v_in²)/2.
| Base case | 2026-10-25T12:30:00Z | Current | - Density scaling: the pressure loss at the solved flow is ρ g h = ΔP_r (ρ/ρ_r)(Q/Q_r)², with ρ the fluid being solved. The operating density cancels out of the head loss h, which the rating alone sets; it only converts head to pressure.
| Base case | 2026-10-25T12:30:00Z | Current | - A Cv or Kv rating is a rated point on water by definition (1 psi at Cv US gpm, 1 bar at Kv m³/h): c = K/(2 g A²) with K from fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01-2007, water at 999.29744568 kg/m³), the valves' conversion, evaluated at a 1 m bore; K ∝ D⁴ makes K/A² the same on every bore, so no pipe diameter is needed. Its pressure loss is (ρ/ρ_w) × 1 psi × (Q/Cv gpm)², or × 1 bar × (Q/Kv m³/h)².
| Base case | 2026-10-25T12:30:00Z | Current | - Reverse flow (outlet → inlet) follows the same, symmetric law and is flagged: no datasheet rates reverse flow.
| Base case | 2026-10-25T12:30:00Z | Current | - Laminar flow (Re < 2000) in the end segment of a connected pipe is flagged, as for a valve's Cv or Kv: the square law is the turbulent-flow law, and the loss is then likely underestimated.
| Base case | 2026-10-25T12:30:00Z | Current | - At zero flow the law's slope 2c¦Q¦ is 0: Newton's Jacobian uses at least 1e-06 x the slopes of the pipes at the element's ports there, as for every link that is not a pipe (EPANET 2.2 bounds such a gradient instead); the law itself is exact.
| Base case | 2026-10-25T12:30:00Z | Current | - Viscosity is not corrected: the loss scales with density only. With a fluid more viscous than the rating's, or at flows well below the rated flow, the real loss may be higher than this law gives (a smooth-tube element dominated by friction scales as ρ^0.75 μ^0.25 Q^1.75 by Blasius' law); a correction needs the equipment's geometry or its vendor's own factors.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
| Base case | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Fluid properties
| Base case | 2026-10-25T12:30:00Z | Current | - Water at 293.15 K: density 998.207 kg/m³, dynamic viscosity 0.0010016 Pa·s, kinematic viscosity 1.0034e-06 m²/s, vapor pressure 2339.32 Pa absolute.
| Base case | 2026-10-25T12:30:00Z | Current | - density: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
| Base case | 2026-10-25T12:30:00Z | Current | - dynamicViscosity: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
| Base case | 2026-10-25T12:30:00Z | Current | - vaporPressure: library, CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
| Base case | 2026-10-25T12:30:00Z | Current | - Properties are constant throughout the network (isothermal).
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Atmosphere and NPSH
| Base case | 2026-10-25T12:30:00Z | Current | - Atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
| Base case | 2026-10-25T12:30:00Z | Current | - NPSH available at the pump suction port = (EGL − z) + (p_atm − p_vap)/(ρg), the absolute static plus velocity head above the vapor pressure; margin = NPSHa − NPSHr, flagged as cavitation when negative.
| Base case | 2026-10-25T12:30:00Z | Current | - Every port's absolute static pressure is checked against the vapor pressure (0 Pa absolute when none is known) and flagged where the liquid would flash.
| Base case | 2026-10-25T12:30:00Z | Current | References:
| Base case | 2026-10-25T12:30:00Z | Current | - U.S. Standard Atmosphere, 1976. NOAA, NASA, USAF, Washington, DC, 1976.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Conventions
| Base case | 2026-10-25T12:30:00Z | Current | - SI units throughout. Pressures are gauge unless labeled absolute; elevations and heads are measured from the single project datum.
| Base case | 2026-10-25T12:30:00Z | Current | - Gauge pressures are relative to the atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
| Base case | 2026-10-25T12:30:00Z | Current | - The energy grade line EGL = z + p/(ρg) + v²/(2g) is the nodal unknown; the hydraulic grade line HGL = EGL − v²/(2g), with v the velocity in the pipe connected at the port. Pump head is the EGL rise.
| Base case | 2026-10-25T12:30:00Z | Current | - Flow is positive from a connection's 'from' port to its 'to' port; branch port flows are positive into the component.
| Base case | 2026-10-25T12:30:00Z | Current | - Every element's trace lists its inputs (with their source: user, default, library or computed), equations, correlations, data sources and intermediate values.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Assumptions
| Base case | 2026-10-25T12:30:00Z | Current | - Steady, incompressible, isothermal, single-phase liquid flow.
| Base case | 2026-10-25T12:30:00Z | Current | - Reservoirs and reference nodes are quiescent bodies of liquid (velocity 0) at a constant head.
| Base case | 2026-10-25T12:30:00Z | Current | - No entrance or exit loss is applied where a pipe meets a reservoir or reference node unless the connection's piping has an entrance fitting (entrance_sharp, entrance_rounded, entrance_projecting) or an exit fitting (exit); without one, the EGL at the port equals the boundary head in either flow direction. The web app adds a sharp-edged entrance where new piping leaves a reservoir and an exit where it enters one (removable), and none at a reference node; each boundary's trace lists the entrance and exit fittings at its ports.
| Base case | 2026-10-25T12:30:00Z | Current | - Fluid properties are constant at the operating temperature.
| Base case | 2026-10-25T12:30:00Z | Current | - Pumps have an integral check: no reverse flow.
| Base case | 2026-10-25T12:30:00Z | Current | - Check valves: a disc that opens fully above the cracking pressure and closes on reverse flow (no partial opening).
| Base case | 2026-10-25T12:30:00Z | Current | - Control valves without an entered resistance are ideal: no loss when fully open.
| Base case | 2026-10-25T12:30:00Z | Current | - Fittings and valves without a user K use the cited correlation for the type at the connected pipe's inner diameter.
| Base case | 2026-10-25T12:30:00Z | Current | - Equipment losses scale with the square of the flow and with density from one rated point, a Cv or a Kv (constant K); viscosity is not corrected.
| Base case | 2026-10-25T12:30:00Z | Current
| Base case | 2026-10-25T12:30:00Z | Current | Software
| Base case | 2026-10-25T12:30:00Z | Current | - CoolProp 8.0.0
| Base case | 2026-10-25T12:30:00Z | Current | - fluids 1.3.1
| Base case | 2026-10-25T12:30:00Z | Current | - numpy 2.5.4
| Base case | 2026-10-25T12:30:00Z | Current | - opensolve-pipe 0.1.0
| Base case | 2026-10-25T12:30:00Z | Current | - scipy 1.18.1
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Calculation methods and assumptions
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Project: Plant water header
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Case: scenario Cv valve (S1)
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | OpenSolve Pipe calculation methods version 1.4.0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Solved: 2026-10-25T12:30:00Z
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Solve status: converged.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Scenario
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Scenario 'Cv valve' (id S1) of this project: 3 of its 3 override(s) of base values were applied to the base project before the network was built, so every result, trace and section below is of the project with those values. Every other value is the base project's; a scenario changes values only, never the components or connections.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Description: The PRV with a Cv 120 trim, a higher low tank and a dirty strainer.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Component PRV1 (control valve): resistance Cv 120 (base: none (the default)).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Component R2 (reservoir): liquid level 6 m (base: 5 m).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Component E1 (equipment): rated pressure drop 40000 Pa (base: 20000 Pa).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - OpenSolve Pipe design decision D15 (CLAUDE.md), from docs/proposals/scenario-manager.md.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Network solution
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Global Gradient Algorithm (Todini & Pilati 1988): Newton's method on the energy grade line at every node and the flow in every link; sparse direct solve of the Schur complement (SciPy SuperLU, splu). One solver for every topology; every connected part needs a reservoir or reference node.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Converged when the largest flow change is at most the project tolerance times the largest flow (plus 1e-14 m³/s), continuity closes at every node and over every component to 1e-09 x the largest flow + 1e-14 m³/s, and the energy equation holds on every link to 1e-07 m. On each link, 8.88178e-16 x the largest magnitude among the energy grade lines at its two ends and its head loss is added to that tolerance (4 x 2.22045e-16, the machine epsilon of double precision): an allowance for the round-off of the heads that the energy residual subtracts, larger than 1e-07 m only where that magnitude exceeds 1e-07 m divided by that factor, about 1.1259e+08 m.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - An active PRV or PSV holds its port's head and passes the flow of the pipe on that port, coupled exactly in Newton's step (EPANET 2.2 lags it by one iteration, which converges the same answer more slowly).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - This project: friction method 'colebrook', flow tolerance 1e-09 (relative to the largest flow), at most 100 Newton iterations per network solve.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - This solve: 10 Newton iterations in 2 outer iteration(s); converged.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Branch components (tees, wyes) are imposed exactly: each one's ports share one head unknown, offset by the branch's path losses (zero for an ideal junction), and its internal flows follow from continuity.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Flows below 1e-12 x the largest flow (plus 1e-14 m³/s) are round-off and reported as zero. Dead-end branches (no way out but the node they hang from) carry no flow by continuity and are reported as exactly zero.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Outer loop for statuses and branch losses: at most 30 counted iterations; an iteration that only holds or releases branch legs at zero flow is not counted (each branch is held a bounded number of times). Once pump and valve statuses repeat after an iteration that changed several of them, one status changes per iteration; a status pattern that still repeats goes back to the latest iteration that asked for several changes and takes one not yet taken, and with none left is reported as not converged, naming the elements that oscillate.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Parts of the network closed off from every reservoir and reference node by closed elements carry no flow and have no computed pressure (flagged).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - A closed-off part that cannot carry zero flow (a pump loop behind a closed valve) has determined flows but no pressure level: its flows and head differences are solved with one node held at an arbitrary head, and its pressures, NPSH available and PRV/PSV setpoint checks are not reported (flagged).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Assigned-flow nodes fix the flow leaving the network at their port (a demand, positive) or entering it (a supply, negative), whatever the pressure there: a nodal demand in the continuity equations, as EPANET's junction demands; their pressure is a result. They are not a fixed-pressure boundary. A dead-end branch to one carries its flow. A part of the network that no reservoir or reference node reaches through open elements carries assigned flows only if they sum to zero (to the continuity tolerance): its flows are then solved and its pressure level is not (flagged); otherwise the closed elements around that part whose status rules open as its pressure falls (a net demand) or rises (a net supply) are re-opened; with none left to open, no steady state carries them, and the solve is reported as not converged, naming the nodes and the elements closed around them (EPANET: a disconnected system). A flow control (an FCV, or a speed-controlled pump) that alone feeds assigned-flow nodes taking its setpoint flow leaves the pressure between them undetermined (reported as not converged, naming them); with another flow the node's flow passes and the control's rules take it to a limit (an FCV fully open below its setpoint, a speed-controlled pump at its maximum or minimum speed), or, above what the control can pass, or with reverse flow through it, no steady state carries it.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Todini, E., and S. Pilati. A gradient algorithm for the analysis of pipe networks. Computer Applications in Water Supply, Vol. 1. Wiley, 1988, 1-20.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Pipe friction
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Darcy–Weisbach head loss h = f (L/D) v²/(2g), g = 9.80665 m/s² (standard gravity, fluids.constants.g), Re = ¦v¦ D/ν.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Laminar, Re < 2000: f = 64/Re (Hagen–Poiseuille).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Turbulent, Re ≥ 4000: the Colebrook (1939) equation, solved exactly with fluids.friction.Clamond (Clamond 2009).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Transition, 2000 ≤ Re < 4000: cubic interpolation between the laminar and turbulent laws (Dunlop's method, as in EPANET 2.2); flagged as transitional flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Flagged outside the cited range: Swamee–Jain beyond its documented 5000 ≤ Re ≤ 1e+08 and 1e-06 ≤ ε/D ≤ 0.05; Colebrook beyond ε/D = 0.05, the largest relative roughness documented for its explicit approximations (fluids.friction.fmethods). ε/D ≥ 3.7 has no Colebrook solution and is rejected.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Pipe dimensions: ASME B36.10M / B36.19M and ASTM D1785 via fluids.piping; roughness: Farshad & Rieke (2006) via fluids.friction.roughness_Farshad; user values where entered (each element's trace names its sources).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Colebrook, C. F. J. ICE 11(4), 1939, 133-156, doi:10.1680/ijoti.1939.13150.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Clamond, D. Ind. Eng. Chem. Res. 48(7), 2009, 3665-3671, doi:10.1021/ie801626g.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Swamee, P. K., and A. K. Jain. J. Hydraulics Div. ASCE 102(5), 1976, 657-664.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Minor losses
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Fitting loss h = n K v²/(2g), K from the cited fluids correlation for the fitting type (data/fittings.json) at the reference pipe's inner diameter; a user K overrides it.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Crane TP-410 K values use the fully turbulent friction factor ft_Crane(D); they are not valid in laminar flow, and a Crane K in a laminar segment is flagged.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Branches
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Tees and wyes with lossModel 'ideal' are junctions without loss, as in EPANET.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - lossModel 'crane': the path losses follow the solved flow split with the Crane TP-410 tee and lateral correlations (fluids.fittings.K_branch_diverging_Crane, K_run_diverging_Crane, K_branch_converging_Crane, K_run_converging_Crane), K on the combined-flow velocity in the run diameter; updated in the outer loop until K changes by less than 0.0001 and the path loss by less than 1e-06 m.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - A tee whose combined flow passes through the branch uses the Darby 3-K tee 'Tee, Through-branch, (as elbow), flanged, (r/D = 1)' per run path on its own velocity (flagged); a wye in that pattern has no cited correlation and is reported as not converged.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Flagged outside the correlations' range: a branch larger than the run (β > 1), unequal run pipes, a wye lateral turning against its lean, and a laminar combined flow (Re < 2000 on the combined-flow velocity in the run diameter: the Crane tee data are for turbulent flow).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Zero flow through a leg: the correlations for flow out through a leg and flow in through it give different port heads in the limit of zero flow. A leg whose flow reverses and reverses back between outer iterations is held at zero flow while the head the network gives its port lies between those two limits; its K is the one its head implies.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - A flow split that keeps alternating across a step of a Crane correlation (a split at which the fluids function switches formula, q = 0.4, 0.5 or 0.6, and K jumps by more than 0.0001) holds K at the mean of the fluids values at the two splits while the solved split stays between them (flagged; the trace lists both values); a split alternating where the correlation is continuous has its K update under-relaxed instead.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Pumps
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Head, efficiency and NPSHr curves: monotone piecewise cubic interpolation (SciPy PchipInterpolator) through the entered points; head and NPSHr are extrapolated along the end slope outside the points (flagged), efficiency is held at its end values (flagged).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Speed: affinity laws, H(Q) = s² H₀(Q/s), NPSHr(Q) = s² NPSHr₀(Q/s), η(Q) = η₀(Q/s).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - No viscosity correction: the curves are used as entered for the fluid (the Hydraulic Institute correction, ANSI/HI 9.6.7, is not in this version).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Integral check: a pump closes when the system head exceeds its shutoff head s² H₀(0) or the flow would reverse (EPANET 2.2 pumpstatus), and is flagged as flow reversal.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - System curve of a pump: at each flow the pump is replaced by that fixed flow and the network solved, every other element following its own law and status rules (other pumps keep running); the system head is EGL(discharge) − EGL(suction). Default flows: 0 to 1.2 x the curve's largest flow x s. Each point starts from the solution at the neighbouring flow (statuses, branch losses and flows; the first from the network's own solve when the solve computes the curves, from the initial state otherwise), so where the statuses or branch patterns admit more than one solution the curve follows one continuously; a point that fails from there is solved from the initial state, and one that still has no head while the flow has a way through (unless a control valve in series is at its switch, below) is solved again from the initial state (if it did not start there) and from it with its active control valves open, the first solve that gives a head, or finds a control valve in series at its switch, being used (with none, the point keeps its first result) and the next point starting from the result used; a flowing point is not solved again when its flow exceeds what every way from the pump's discharge back to its suction can pass that way (an FCV at most its setpoint, a check valve, PRV, PSV or pump nothing in reverse: a cut, Ford and Fulkerson), since no steady state carries it, and one whose flow is that limit, where every steady state passes each FCV of the cut at its setpoint, is also solved with each such FCV held open, to find whether it sits at its switch. A point has no head where no steady state carries its flow, where its head is undetermined (a side of the pump with no fixed pressure, or a control valve in series at its switch, which could also hold the flow throttled with any higher head) or where its solve does not converge; its message says which. With assigned-flow nodes, the cut counts their flows as fixed demands and supplies (Gale): a demand on the pump's side of the cut takes part of the forced flow, and one beyond it adds to what the cut must pass. Read the other way, the cut bounds the flow from below: a flowing point below the least flow that assigned flows need through the pump (a demand on its discharge side that a one-way element keeps every reservoir and reference node from feeding, or a supply on its suction side that one keeps from draining) has no steady state either and is not solved again, and one at that floor is solved with each FCV of the cut held open too. A side of the pump that reaches only assigned-flow nodes has no point with a head.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and R. E. Carlson. Monotone piecewise cubic interpolation. SIAM J. Numer. Anal. 17(2), 1980, 238-246.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and J. Butland. A method for constructing local monotone piecewise cubic interpolants. SIAM J. Sci. Stat. Comput. 5(2), 1984, 300-304, doi:10.1137/0905021 (the derivative formula of scipy.interpolate.PchipInterpolator).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Ford, L. R., and D. R. Fulkerson. Maximal flow through a network. Canadian Journal of Mathematics 8, 1956, 399-404 (the max-flow min-cut theorem: the flows no state carries through a pump on its system curve).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Gale, D. A theorem on flows in networks. Pacific Journal of Mathematics 7(2), 1957, 1073-1082 (a flow with fixed supplies and demands exists when no node set holds more net supply than its cut can pass: the assigned flows in a pump's system-curve bounds).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Valves
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Open valve loss h = K v²/(2g) on the inlet pipe's inner diameter; Cv and Kv converted with fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01, turbulent flow, without the Reynolds number factor F_R); without a resistance, the Crane TP-410 full-bore K for the valve type. A Cv, Kv or Crane K in laminar flow (Re < 2000 in the inlet pipe) is flagged.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Active check valves: open loss h = Δp_crack/(ρg) + K v²/(2g); open above their cracking head and close on reverse flow (EPANET 2.2 cvstatus with the cracking head). A check valve locked open by the user has the open loss K v²/(2g) only, with no cracking head and no check action; locked closed, it passes no flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - PRV, PSV and FCV hold the outlet static pressure, inlet static pressure or flow when active; status rules from EPANET 2.2 (hydstatus.c) applied to the energy grade line, with the setpoint head z + p/(ρg) + v²/(2g) at the port; an FCV closes on reverse flow (EPANET's would pass it), and an active FCV opens once the head across it is below its fully open loss at the setpoint (EPANET's waits for a reverse head), as the PRV and PSV rules do. Control valves without a resistance: ideal control valve: no loss when fully open (K = 0); give a resistance for a real valve.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Status tolerances: 0.0001 m in head, 1e-08 m³/s in flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - An active state with no solution falls back to the states the valve rules give at that solve's first iterations (EPANET 2.2 applies them at every iteration), then to open and closed valves (EPANET's badvalve).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - A section closed off by closed pumps or valves carries no flow and has no computed pressure; the closed elements around it are re-tested against the heads it can take at zero flow (a dead-headed pump puts its shutoff head on it), and re-opened when no such head keeps them all closed. A PRV or PSV inside such a section or one whose pressure level is undetermined, or closed between two of them, keeps its state only if one set of section levels holds it together with those closed elements and the other such valves; otherwise the fewest of these elements change, each to the state its rule gives at levels that hold the others (a PRV or PSV that could not be active there, with no fixed head to draw from or deliver to, closes if open and opens if closed).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Equipment
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Equipment (one side of a heat exchanger, a coil, a strainer, a filter, or another passive element given by its datasheet): the loss of total head from its inlet to its outlet is h = EGL_in − EGL_out = c Q¦Q¦ (a loss of total pressure ρ g h), with c = ΔP_r/(ρ_r g Q_r²) from the rated pressure drop ΔP_r at the rated flow Q_r for a fluid of density ρ_r: a constant K, the square law of ISA-75.01.01-2007 eq. (1) for non-choked, turbulent liquid flow, and the high-Re limit of the 3-K method (Silverberg & Darby). The rated drop is the dissipative loss (friction and form) of total pressure between the ports, without the static head between them: each port's static pressure follows from its EGL with the velocity in its connected pipe, so the static drop reported is ρ g h + ρ g (z_out − z_in) + ρ (v_out² − v_in²)/2.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Density scaling: the pressure loss at the solved flow is ρ g h = ΔP_r (ρ/ρ_r)(Q/Q_r)², with ρ the fluid being solved. The operating density cancels out of the head loss h, which the rating alone sets; it only converts head to pressure.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - A Cv or Kv rating is a rated point on water by definition (1 psi at Cv US gpm, 1 bar at Kv m³/h): c = K/(2 g A²) with K from fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01-2007, water at 999.29744568 kg/m³), the valves' conversion, evaluated at a 1 m bore; K ∝ D⁴ makes K/A² the same on every bore, so no pipe diameter is needed. Its pressure loss is (ρ/ρ_w) × 1 psi × (Q/Cv gpm)², or × 1 bar × (Q/Kv m³/h)².
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Reverse flow (outlet → inlet) follows the same, symmetric law and is flagged: no datasheet rates reverse flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Laminar flow (Re < 2000) in the end segment of a connected pipe is flagged, as for a valve's Cv or Kv: the square law is the turbulent-flow law, and the loss is then likely underestimated.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - At zero flow the law's slope 2c¦Q¦ is 0: Newton's Jacobian uses at least 1e-06 x the slopes of the pipes at the element's ports there, as for every link that is not a pipe (EPANET 2.2 bounds such a gradient instead); the law itself is exact.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Viscosity is not corrected: the loss scales with density only. With a fluid more viscous than the rating's, or at flows well below the rated flow, the real loss may be higher than this law gives (a smooth-tube element dominated by friction scales as ρ^0.75 μ^0.25 Q^1.75 by Blasius' law); a correction needs the equipment's geometry or its vendor's own factors.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Fluid properties
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Water at 293.15 K: density 998.207 kg/m³, dynamic viscosity 0.0010016 Pa·s, kinematic viscosity 1.0034e-06 m²/s, vapor pressure 2339.32 Pa absolute.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - density: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - dynamicViscosity: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - vaporPressure: library, CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Properties are constant throughout the network (isothermal).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Atmosphere and NPSH
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - NPSH available at the pump suction port = (EGL − z) + (p_atm − p_vap)/(ρg), the absolute static plus velocity head above the vapor pressure; margin = NPSHa − NPSHr, flagged as cavitation when negative.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Every port's absolute static pressure is checked against the vapor pressure (0 Pa absolute when none is known) and flagged where the liquid would flash.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | References:
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - U.S. Standard Atmosphere, 1976. NOAA, NASA, USAF, Washington, DC, 1976.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Conventions
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - SI units throughout. Pressures are gauge unless labeled absolute; elevations and heads are measured from the single project datum.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Gauge pressures are relative to the atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - The energy grade line EGL = z + p/(ρg) + v²/(2g) is the nodal unknown; the hydraulic grade line HGL = EGL − v²/(2g), with v the velocity in the pipe connected at the port. Pump head is the EGL rise.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Flow is positive from a connection's 'from' port to its 'to' port; branch port flows are positive into the component.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Every element's trace lists its inputs (with their source: user, default, library or computed), equations, correlations, data sources and intermediate values.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Assumptions
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Steady, incompressible, isothermal, single-phase liquid flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Reservoirs and reference nodes are quiescent bodies of liquid (velocity 0) at a constant head.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - No entrance or exit loss is applied where a pipe meets a reservoir or reference node unless the connection's piping has an entrance fitting (entrance_sharp, entrance_rounded, entrance_projecting) or an exit fitting (exit); without one, the EGL at the port equals the boundary head in either flow direction. The web app adds a sharp-edged entrance where new piping leaves a reservoir and an exit where it enters one (removable), and none at a reference node; each boundary's trace lists the entrance and exit fittings at its ports.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Fluid properties are constant at the operating temperature.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Pumps have an integral check: no reverse flow.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Check valves: a disc that opens fully above the cracking pressure and closes on reverse flow (no partial opening).
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Control valves without an entered resistance are ideal: no loss when fully open.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Fittings and valves without a user K use the cited correlation for the type at the connected pipe's inner diameter.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - Equipment losses scale with the square of the flow and with density from one rated point, a Cv or a Kv (constant K); viscosity is not corrected.
S1 | Cv valve | 2026-10-25T12:30:00Z | Current
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | Software
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - CoolProp 8.0.0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - fluids 1.3.1
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - numpy 2.5.4
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - opensolve-pipe 0.1.0
S1 | Cv valve | 2026-10-25T12:30:00Z | Current | - scipy 1.18.1
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Calculation methods and assumptions
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Project: Plant water header
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Case: scenario Supply at AF1 (S2)
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | OpenSolve Pipe calculation methods version 1.4.0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Solved: 2026-10-25T12:30:00Z
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Solve status: converged.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Scenario
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Scenario 'Supply at AF1' (id S2) of this project: 2 of its 2 override(s) of base values were applied to the base project before the network was built, so every result, trace and section below is of the project with those values. Every other value is the base project's; a scenario changes values only, never the components or connections.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Component AF1 (assigned-flow node): assigned flow -0.002 m³/s (base: 0.003 m³/s).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Connection L4, pipe 1: length 25 m (base: 15 m).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - OpenSolve Pipe design decision D15 (CLAUDE.md), from docs/proposals/scenario-manager.md.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Network solution
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Global Gradient Algorithm (Todini & Pilati 1988): Newton's method on the energy grade line at every node and the flow in every link; sparse direct solve of the Schur complement (SciPy SuperLU, splu). One solver for every topology; every connected part needs a reservoir or reference node.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Converged when the largest flow change is at most the project tolerance times the largest flow (plus 1e-14 m³/s), continuity closes at every node and over every component to 1e-09 x the largest flow + 1e-14 m³/s, and the energy equation holds on every link to 1e-07 m. On each link, 8.88178e-16 x the largest magnitude among the energy grade lines at its two ends and its head loss is added to that tolerance (4 x 2.22045e-16, the machine epsilon of double precision): an allowance for the round-off of the heads that the energy residual subtracts, larger than 1e-07 m only where that magnitude exceeds 1e-07 m divided by that factor, about 1.1259e+08 m.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - An active PRV or PSV holds its port's head and passes the flow of the pipe on that port, coupled exactly in Newton's step (EPANET 2.2 lags it by one iteration, which converges the same answer more slowly).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - This project: friction method 'colebrook', flow tolerance 1e-09 (relative to the largest flow), at most 100 Newton iterations per network solve.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - This solve: 10 Newton iterations in 2 outer iteration(s); converged.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Branch components (tees, wyes) are imposed exactly: each one's ports share one head unknown, offset by the branch's path losses (zero for an ideal junction), and its internal flows follow from continuity.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Flows below 1e-12 x the largest flow (plus 1e-14 m³/s) are round-off and reported as zero. Dead-end branches (no way out but the node they hang from) carry no flow by continuity and are reported as exactly zero.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Outer loop for statuses and branch losses: at most 30 counted iterations; an iteration that only holds or releases branch legs at zero flow is not counted (each branch is held a bounded number of times). Once pump and valve statuses repeat after an iteration that changed several of them, one status changes per iteration; a status pattern that still repeats goes back to the latest iteration that asked for several changes and takes one not yet taken, and with none left is reported as not converged, naming the elements that oscillate.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Parts of the network closed off from every reservoir and reference node by closed elements carry no flow and have no computed pressure (flagged).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - A closed-off part that cannot carry zero flow (a pump loop behind a closed valve) has determined flows but no pressure level: its flows and head differences are solved with one node held at an arbitrary head, and its pressures, NPSH available and PRV/PSV setpoint checks are not reported (flagged).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Assigned-flow nodes fix the flow leaving the network at their port (a demand, positive) or entering it (a supply, negative), whatever the pressure there: a nodal demand in the continuity equations, as EPANET's junction demands; their pressure is a result. They are not a fixed-pressure boundary. A dead-end branch to one carries its flow. A part of the network that no reservoir or reference node reaches through open elements carries assigned flows only if they sum to zero (to the continuity tolerance): its flows are then solved and its pressure level is not (flagged); otherwise the closed elements around that part whose status rules open as its pressure falls (a net demand) or rises (a net supply) are re-opened; with none left to open, no steady state carries them, and the solve is reported as not converged, naming the nodes and the elements closed around them (EPANET: a disconnected system). A flow control (an FCV, or a speed-controlled pump) that alone feeds assigned-flow nodes taking its setpoint flow leaves the pressure between them undetermined (reported as not converged, naming them); with another flow the node's flow passes and the control's rules take it to a limit (an FCV fully open below its setpoint, a speed-controlled pump at its maximum or minimum speed), or, above what the control can pass, or with reverse flow through it, no steady state carries it.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Todini, E., and S. Pilati. A gradient algorithm for the analysis of pipe networks. Computer Applications in Water Supply, Vol. 1. Wiley, 1988, 1-20.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Pipe friction
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Darcy–Weisbach head loss h = f (L/D) v²/(2g), g = 9.80665 m/s² (standard gravity, fluids.constants.g), Re = ¦v¦ D/ν.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Laminar, Re < 2000: f = 64/Re (Hagen–Poiseuille).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Turbulent, Re ≥ 4000: the Colebrook (1939) equation, solved exactly with fluids.friction.Clamond (Clamond 2009).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Transition, 2000 ≤ Re < 4000: cubic interpolation between the laminar and turbulent laws (Dunlop's method, as in EPANET 2.2); flagged as transitional flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Flagged outside the cited range: Swamee–Jain beyond its documented 5000 ≤ Re ≤ 1e+08 and 1e-06 ≤ ε/D ≤ 0.05; Colebrook beyond ε/D = 0.05, the largest relative roughness documented for its explicit approximations (fluids.friction.fmethods). ε/D ≥ 3.7 has no Colebrook solution and is rejected.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Pipe dimensions: ASME B36.10M / B36.19M and ASTM D1785 via fluids.piping; roughness: Farshad & Rieke (2006) via fluids.friction.roughness_Farshad; user values where entered (each element's trace names its sources).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Colebrook, C. F. J. ICE 11(4), 1939, 133-156, doi:10.1680/ijoti.1939.13150.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Clamond, D. Ind. Eng. Chem. Res. 48(7), 2009, 3665-3671, doi:10.1021/ie801626g.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Swamee, P. K., and A. K. Jain. J. Hydraulics Div. ASCE 102(5), 1976, 657-664.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2 User Manual. US EPA, 2020 (source: src/hydcoeffs.c).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Minor losses
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Fitting loss h = n K v²/(2g), K from the cited fluids correlation for the fitting type (data/fittings.json) at the reference pipe's inner diameter; a user K overrides it.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Crane TP-410 K values use the fully turbulent friction factor ft_Crane(D); they are not valid in laminar flow, and a Crane K in a laminar segment is flagged.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Rennels, D. C., and H. M. Hudson. Pipe Flow: A Practical and Comprehensive Guide. Wiley, 2012.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Branches
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Tees and wyes with lossModel 'ideal' are junctions without loss, as in EPANET.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - lossModel 'crane': the path losses follow the solved flow split with the Crane TP-410 tee and lateral correlations (fluids.fittings.K_branch_diverging_Crane, K_run_diverging_Crane, K_branch_converging_Crane, K_run_converging_Crane), K on the combined-flow velocity in the run diameter; updated in the outer loop until K changes by less than 0.0001 and the path loss by less than 1e-06 m.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - A tee whose combined flow passes through the branch uses the Darby 3-K tee 'Tee, Through-branch, (as elbow), flanged, (r/D = 1)' per run path on its own velocity (flagged); a wye in that pattern has no cited correlation and is reported as not converged.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Flagged outside the correlations' range: a branch larger than the run (β > 1), unequal run pipes, a wye lateral turning against its lean, and a laminar combined flow (Re < 2000 on the combined-flow velocity in the run diameter: the Crane tee data are for turbulent flow).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Zero flow through a leg: the correlations for flow out through a leg and flow in through it give different port heads in the limit of zero flow. A leg whose flow reverses and reverses back between outer iterations is held at zero flow while the head the network gives its port lies between those two limits; its K is the one its head implies.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - A flow split that keeps alternating across a step of a Crane correlation (a split at which the fluids function switches formula, q = 0.4, 0.5 or 0.6, and K jumps by more than 0.0001) holds K at the mean of the fluids values at the two splits while the solved split stays between them (flagged; the trace lists both values); a split alternating where the correlation is continuous has its K update under-relaxed instead.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Pumps
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Head, efficiency and NPSHr curves: monotone piecewise cubic interpolation (SciPy PchipInterpolator) through the entered points; head and NPSHr are extrapolated along the end slope outside the points (flagged), efficiency is held at its end values (flagged).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Speed: affinity laws, H(Q) = s² H₀(Q/s), NPSHr(Q) = s² NPSHr₀(Q/s), η(Q) = η₀(Q/s).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - No viscosity correction: the curves are used as entered for the fluid (the Hydraulic Institute correction, ANSI/HI 9.6.7, is not in this version).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Integral check: a pump closes when the system head exceeds its shutoff head s² H₀(0) or the flow would reverse (EPANET 2.2 pumpstatus), and is flagged as flow reversal.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - System curve of a pump: at each flow the pump is replaced by that fixed flow and the network solved, every other element following its own law and status rules (other pumps keep running); the system head is EGL(discharge) − EGL(suction). Default flows: 0 to 1.2 x the curve's largest flow x s. Each point starts from the solution at the neighbouring flow (statuses, branch losses and flows; the first from the network's own solve when the solve computes the curves, from the initial state otherwise), so where the statuses or branch patterns admit more than one solution the curve follows one continuously; a point that fails from there is solved from the initial state, and one that still has no head while the flow has a way through (unless a control valve in series is at its switch, below) is solved again from the initial state (if it did not start there) and from it with its active control valves open, the first solve that gives a head, or finds a control valve in series at its switch, being used (with none, the point keeps its first result) and the next point starting from the result used; a flowing point is not solved again when its flow exceeds what every way from the pump's discharge back to its suction can pass that way (an FCV at most its setpoint, a check valve, PRV, PSV or pump nothing in reverse: a cut, Ford and Fulkerson), since no steady state carries it, and one whose flow is that limit, where every steady state passes each FCV of the cut at its setpoint, is also solved with each such FCV held open, to find whether it sits at its switch. A point has no head where no steady state carries its flow, where its head is undetermined (a side of the pump with no fixed pressure, or a control valve in series at its switch, which could also hold the flow throttled with any higher head) or where its solve does not converge; its message says which. With assigned-flow nodes, the cut counts their flows as fixed demands and supplies (Gale): a demand on the pump's side of the cut takes part of the forced flow, and one beyond it adds to what the cut must pass. Read the other way, the cut bounds the flow from below: a flowing point below the least flow that assigned flows need through the pump (a demand on its discharge side that a one-way element keeps every reservoir and reference node from feeding, or a supply on its suction side that one keeps from draining) has no steady state either and is not solved again, and one at that floor is solved with each FCV of the cut held open too. A side of the pump that reaches only assigned-flow nodes has no point with a head.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and R. E. Carlson. Monotone piecewise cubic interpolation. SIAM J. Numer. Anal. 17(2), 1980, 238-246.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Fritsch, F. N., and J. Butland. A method for constructing local monotone piecewise cubic interpolants. SIAM J. Sci. Stat. Comput. 5(2), 1984, 300-304, doi:10.1137/0905021 (the derivative formula of scipy.interpolate.PchipInterpolator).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Ford, L. R., and D. R. Fulkerson. Maximal flow through a network. Canadian Journal of Mathematics 8, 1956, 399-404 (the max-flow min-cut theorem: the flows no state carries through a pump on its system curve).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Gale, D. A theorem on flows in networks. Pacific Journal of Mathematics 7(2), 1957, 1073-1082 (a flow with fixed supplies and demands exists when no node set holds more net supply than its cut can pass: the assigned flows in a pump's system-curve bounds).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Valves
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Open valve loss h = K v²/(2g) on the inlet pipe's inner diameter; Cv and Kv converted with fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01, turbulent flow, without the Reynolds number factor F_R); without a resistance, the Crane TP-410 full-bore K for the valve type. A Cv, Kv or Crane K in laminar flow (Re < 2000 in the inlet pipe) is flagged.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Active check valves: open loss h = Δp_crack/(ρg) + K v²/(2g); open above their cracking head and close on reverse flow (EPANET 2.2 cvstatus with the cracking head). A check valve locked open by the user has the open loss K v²/(2g) only, with no cracking head and no check action; locked closed, it passes no flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - PRV, PSV and FCV hold the outlet static pressure, inlet static pressure or flow when active; status rules from EPANET 2.2 (hydstatus.c) applied to the energy grade line, with the setpoint head z + p/(ρg) + v²/(2g) at the port; an FCV closes on reverse flow (EPANET's would pass it), and an active FCV opens once the head across it is below its fully open loss at the setpoint (EPANET's waits for a reverse head), as the PRV and PSV rules do. Control valves without a resistance: ideal control valve: no loss when fully open (K = 0); give a resistance for a real valve.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Status tolerances: 0.0001 m in head, 1e-08 m³/s in flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - An active state with no solution falls back to the states the valve rules give at that solve's first iterations (EPANET 2.2 applies them at every iteration), then to open and closed valves (EPANET's badvalve).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - A section closed off by closed pumps or valves carries no flow and has no computed pressure; the closed elements around it are re-tested against the heads it can take at zero flow (a dead-headed pump puts its shutoff head on it), and re-opened when no such head keeps them all closed. A PRV or PSV inside such a section or one whose pressure level is undetermined, or closed between two of them, keeps its state only if one set of section levels holds it together with those closed elements and the other such valves; otherwise the fewest of these elements change, each to the state its rule gives at levels that hold the others (a PRV or PSV that could not be active there, with no fixed head to draw from or deliver to, closes if open and opens if closed).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Rossman, L. A., et al. EPANET 2.2. US EPA, 2020 (source: src/hydstatus.c, status rules).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Crane Co. TP-410 Flow of Fluids Through Valves, Fittings, and Pipe, 2009.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Equipment
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Equipment (one side of a heat exchanger, a coil, a strainer, a filter, or another passive element given by its datasheet): the loss of total head from its inlet to its outlet is h = EGL_in − EGL_out = c Q¦Q¦ (a loss of total pressure ρ g h), with c = ΔP_r/(ρ_r g Q_r²) from the rated pressure drop ΔP_r at the rated flow Q_r for a fluid of density ρ_r: a constant K, the square law of ISA-75.01.01-2007 eq. (1) for non-choked, turbulent liquid flow, and the high-Re limit of the 3-K method (Silverberg & Darby). The rated drop is the dissipative loss (friction and form) of total pressure between the ports, without the static head between them: each port's static pressure follows from its EGL with the velocity in its connected pipe, so the static drop reported is ρ g h + ρ g (z_out − z_in) + ρ (v_out² − v_in²)/2.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Density scaling: the pressure loss at the solved flow is ρ g h = ΔP_r (ρ/ρ_r)(Q/Q_r)², with ρ the fluid being solved. The operating density cancels out of the head loss h, which the rating alone sets; it only converts head to pressure.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - A Cv or Kv rating is a rated point on water by definition (1 psi at Cv US gpm, 1 bar at Kv m³/h): c = K/(2 g A²) with K from fluids.fittings.Cv_to_K / Kv_to_K (ISA-75.01.01-2007, water at 999.29744568 kg/m³), the valves' conversion, evaluated at a 1 m bore; K ∝ D⁴ makes K/A² the same on every bore, so no pipe diameter is needed. Its pressure loss is (ρ/ρ_w) × 1 psi × (Q/Cv gpm)², or × 1 bar × (Q/Kv m³/h)².
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Reverse flow (outlet → inlet) follows the same, symmetric law and is flagged: no datasheet rates reverse flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Laminar flow (Re < 2000) in the end segment of a connected pipe is flagged, as for a valve's Cv or Kv: the square law is the turbulent-flow law, and the loss is then likely underestimated.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - At zero flow the law's slope 2c¦Q¦ is 0: Newton's Jacobian uses at least 1e-06 x the slopes of the pipes at the element's ports there, as for every link that is not a pipe (EPANET 2.2 bounds such a gradient instead); the law itself is exact.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Viscosity is not corrected: the loss scales with density only. With a fluid more viscous than the rating's, or at flows well below the rated flow, the real loss may be higher than this law gives (a smooth-tube element dominated by friction scales as ρ^0.75 μ^0.25 Q^1.75 by Blasius' law); a correction needs the equipment's geometry or its vendor's own factors.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - ISA-75.01.01-2007 (60534-2-1 Mod), Flow Equations for Sizing Control Valves.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Silverberg, P., and R. Darby. Correlate pressure drops through fittings. Chem. Eng. 106(7), 1999, 101.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Fluid properties
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Water at 293.15 K: density 998.207 kg/m³, dynamic viscosity 0.0010016 Pa·s, kinematic viscosity 1.0034e-06 m²/s, vapor pressure 2339.32 Pa absolute.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - density: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - dynamicViscosity: library, CoolProp 8.0.0 'Water' (HEOS), liquid at 293.15 K, 101325 Pa: M. L. Huber et al., 'New International Formulation for the Viscosity of H2O', J. Phys. Chem. Ref. Data 38 (2009) 101-125, doi:10.1063/1.3088050
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - vaporPressure: library, CoolProp 8.0.0 'Water' (HEOS), saturation pressure at 293.15 K: IAPWS-95: W. Wagner and A. Pruß, 'The IAPWS Formulation 1995 for the Thermodynamic Properties of Ordinary Water Substance for General and Scientific Use', J. Phys. Chem. Ref. Data 31 (2002) 387-535, doi:10.1063/1.1461829
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Properties are constant throughout the network (isothermal).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Atmosphere and NPSH
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - NPSH available at the pump suction port = (EGL − z) + (p_atm − p_vap)/(ρg), the absolute static plus velocity head above the vapor pressure; margin = NPSHa − NPSHr, flagged as cavitation when negative.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Every port's absolute static pressure is checked against the vapor pressure (0 Pa absolute when none is known) and flagged where the liquid would flash.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | References:
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - U.S. Standard Atmosphere, 1976. NOAA, NASA, USAF, Washington, DC, 1976.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Conventions
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - SI units throughout. Pressures are gauge unless labeled absolute; elevations and heads are measured from the single project datum.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Gauge pressures are relative to the atmospheric pressure: US Standard Atmosphere 1976 at the site elevation 120 m (fluids.atmosphere.ATMOSPHERE_1976).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - The energy grade line EGL = z + p/(ρg) + v²/(2g) is the nodal unknown; the hydraulic grade line HGL = EGL − v²/(2g), with v the velocity in the pipe connected at the port. Pump head is the EGL rise.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Flow is positive from a connection's 'from' port to its 'to' port; branch port flows are positive into the component.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Every element's trace lists its inputs (with their source: user, default, library or computed), equations, correlations, data sources and intermediate values.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Assumptions
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Steady, incompressible, isothermal, single-phase liquid flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Reservoirs and reference nodes are quiescent bodies of liquid (velocity 0) at a constant head.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - No entrance or exit loss is applied where a pipe meets a reservoir or reference node unless the connection's piping has an entrance fitting (entrance_sharp, entrance_rounded, entrance_projecting) or an exit fitting (exit); without one, the EGL at the port equals the boundary head in either flow direction. The web app adds a sharp-edged entrance where new piping leaves a reservoir and an exit where it enters one (removable), and none at a reference node; each boundary's trace lists the entrance and exit fittings at its ports.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Fluid properties are constant at the operating temperature.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Pumps have an integral check: no reverse flow.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Check valves: a disc that opens fully above the cracking pressure and closes on reverse flow (no partial opening).
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Control valves without an entered resistance are ideal: no loss when fully open.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Fittings and valves without a user K use the cited correlation for the type at the connected pipe's inner diameter.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - Equipment losses scale with the square of the flow and with density from one rated point, a Cv or a Kv (constant K); viscosity is not corrected.
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | Software
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - CoolProp 8.0.0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - fluids 1.3.1
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - numpy 2.5.4
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - opensolve-pipe 0.1.0
S2 | Supply at AF1 | 2026-10-25T12:30:00Z | Current | - scipy 1.18.1